## FUNCTIONS
HOLDING REGISTERS | FUNC_CODE
FACTORY_DRIVER | 0x03,0x06,0x10
FACTORY_SET | 0x03,0x06,0x10
SERVICE | 0x03,0x06,0x10
SERVICE_HARD | 0x03,0x06,0x10
SHARE | 0x03,0x06,0x10
TIME_DRIVER | 0x03,0x06,0x10
TIME_SWITCH_WEEK | 0x03,0x06,0x10
TIME_SWITCH_YEAR | 0x03,0x06,0x10
ERROR_LOG_AHU | 0x03,0x06,0x10
ERROR_LOG_AC | 0x03,0x06,0x10
ERROR_LOG_DRIVER | 0x03,0x06,0x10
NETWORK | 0x03,0x06,0x10
CFG_UNIT | 0x03,0x06,0x10
WIFI_SETTINGS | 0x03,0x06,0x10
DIRECT_CONTROL | 0x03,0x06,0x10
NORDIC_SERVICE | 0x03,0x06,0x10
INPUT REGISTERS
INFO | 0x04
STATUS_AHU | 0x04
STATUS_AC | 0x04
SLAVE_AC_STATUS | 0x04
TIME | 0x04
Default modbus settings
Modbus Unit Address | 1
Baudrate | 9600
Parity | ODD
Stop Bits | 1
PLC Addresses - BASE1
NITE:
Used for HRU and AHU -green
Used for Air curtains, IC controllers and SC controllers - orange
Used for all products - without color marking

## FACTORY_DRIVER (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Factory_driver register - without valid FactoryPass only read (Factory reset no effect)
10000 | FactoryPass |  |  | 0 | 0xFFFF | 0
10001 | FactoryReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10002 | HardFactoryReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10003 | SWReset |  | 0 - non 1 - active | 0 | 1 | 0 | RESET_NON ACTIVE
10004 | FwMbUpdateFlag |  | 0 - non 0xAB16- request | 0 | 0xFFFF | 0 | UPDATEFLAG_NON REQUEST
10005 | FwCpUpdateFlag |  | 0 - non 0xAB17 - request | 0 | 0xFFFF | 0 | UPDATEFLAG_NON REQUEST

## FACTORY_SET (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Factory_set register - without valid FactoryPass only read (Factory reset no effect)
10100 | FactoryPass |  |  | 0 | 0xFFFF | 0
10101 | Mode |  | 0-2vv 1-FranceAir 2-USA 3-Helios | 0 | 3 | 0 | HOME_2VV USA FRANCEAIR HELIOS
10102 | Locality |  | 0-EU 1-USA | 0 | 1 | 0 | LOC_EU LOC_USA
10103 | ModuleB |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10104 | Module1W |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10105 | ModuleEnergyMeasure |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10106 | ModuleRotaryRecup |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10107 | ModuleAC3 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10108 | ModuleAC5 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10109 | ModuleAC5_400 |  | 0 - non 1 - fitted | 0 | 1 | 0 | MODULE_NON FITTED
10110 | EhternetModule |  | 0 - non 1 - fitted | 0 | 1 | 1 | MODULE_NON FITTED
10111 | MaxFlowManual |  | ‰ of fan power | 700 | 1000 | 1000
10112 | MinFlowManual |  | ‰ of fan power | 0 | 400 | 200
10113 | StepFlowManual |  | ‰ of fan power | 10 | 200 | 100
10114 | MaxFlow |  | m3/h (cfm) | 150 (90) | 700 (420) | 150 (100) | 150 (90) 300 (180) 500 (300) 700 (420)
10115 | MinFlow |  | m3/h (cfm) | 40 (20) | 140 (80) | 40 (20) | 40 (20) 70 (40) 100 (60) 140 (80)
10116 | StepFlow |  | m3/h (cfm) | 11 (6) | 56 (32) | 11 (6) | 11 (6) 23 (13) 40 (23) 56 (32)
10117 | UnitSpecif |  | 0 - vertical 1 - horizontal 2- flat 3 - rooftop 4 - wall | 0 | 4 | 4 | VERTICAL HORIZONTAL FLAT ROOFTOP WALL
10118 | Preheater_set_1 |  | 0 - PWM 1 - analog | 0 | 1 | 1 | SET_PWM SET_ANALOG
10119 | Preheater_1 |  | 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
10120 | Preheater_set_2 |  | 0 - PWM 1 - analog | 0 | 1 | 1 | SET_PWM SET_ANALOG
10121 | Preheater_2 |  | 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
10122 | Postheat_set_1 |  | 0 - PWM 1 - analog | 0 | 1 | 0 | SET_PWM SET_ANALOG
10123 | Postheat_1 |  | 0 - none 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
10124 | Postheat_set_2 |  | 0 - PWM (module B) 1 - analog | 0 | 1 | 0 | SET_PWM SET_ANALOG
10125 | Postheat_2 |  | 0 - none (module B) 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
10126 | HEPA_filter_used |  | 0 - non 1 - mount | 0 | 0 | 0 | HEPA_NON HEPA_MOUNT
10127 | reserva |  |  | 0 | 0 | 0
10128 | Recirculation |  | 0 - non 1 - mount | 0 | 0 | 0 | RECIRCULATION_NON MOUNT
10129 | Bypass |  | 0 - non 1 - stepless 0 - 10V 2 - OPEN/CLOSE | 0 | 2 | 1 | BYPASS_NON STEPLESS_10V OPEN_CLOSE
10130 | RecupType |  | 0 - non 1 - plate exchanger 2 - rotary wheel 3 - enthalpy plate | 0 | 3 | 1 | RECUPTYPE_NON PLATE EXCHANGER ROTARY WHEEL ENTHALPY PLATE
10131 | ADBmodule |  | 0 - non 1 - internal 2 - external | 0 | 2 | 0 | ADBMODUL_NON INTERNAL EXTERNAL
10132 | MotorType |  | 0 - EC 1 - AC 2 - DC | 0 | 2 | 0 | MOTORTYPE_EC MOTORTYPE_AC MOTORTYPE_DC
10133 | MotorSpecific |  | 0 - EBM 1 - FansTech | 0 | 1 | 0 | EBM FANSTECH
10134 | MotorEC_set |  | 0 - PWM 1 - analog (0-10V) | 0 | 1 | 0 | EC_PWM EC_ANALOG
10135 | SensorFilterIn |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10136 | SensorFilterOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10137 | SensorFanInlet |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10138 | SensorFanOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10139 | SensorDuct |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10140 | SensorC4 |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10141 | SensorRH |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10142 | SensorRHRec |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10143 | SensorAQS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10144 | TempEXT1 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10145 | TempEXT2 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10146 | TempEXT3 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10147 | TempEXT4 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10148 | TempINT0 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10149 | TempINT1 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10150 | TempINT2 |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10151 | TempWIn |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10152 | TempWOut |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10153 | TempRoom |  | 0 - non 1 - used | 0 | 1 | 1 | SENZOR_NON USED
10154 | HeaterAlarm1 |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10155 | HeaterAlarm2 |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10156 | Inlet_fan |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10157 | Outlet_fan |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10158 | A_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10159 | G_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10160 | Xxx_module |  | 0 - non | 0 | 1 | 0 | non
|  |  | 1 - used |  |  |  | used
10161 | Room BMS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10162 | EXT1 BMS |  | 0 - non 1 - used | 0 | 1 | 0 | SENZOR_NON USED
10163 | FilterDisableStatus |  | 0 - FILTER_ALL_ACTIVE 1 -FILTER_DISABLE_INLET 2 - FILTER_DISABLE_OUTLET | 0 | 2 | 0
10164 | Reserva |  |  | 0 | 0 | 0

## SERVICE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Service register (Factory reset set to default)
20001 | HighCO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 1100
20002 | LowCO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 350
20003 | HighCO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 2000
20004 | LowCO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 350
20005 | HighAQSLevelUni |  | % | 0 | 100 | 100
20006 | LowAQSLevelUni |  | % | 0 | 100 | 0
20007 | FlowOfset |  | % | -100 | 50 | 0
20008 | Reserva |  |  | 0 | 0 | 0
20009 | NoBodyTimeOut |  | min | 1 | 60 | 30
20010 | NobodyFlow |  | % | 20 | 50 | 20
20011 | BoostFromOff |  | 0 - Boost from run (only) 1 - Boost from off | 0 | 1 | 0 | BOOST_FROM_RUN BOOST_FROM_OFF
20012 | BoostTimer |  | min | 1 | 60 | 3
20013 | BoostFlow |  | % | 0 | 100 | 100
20014 | FreecoolingEnable |  | 0 - disable 1 - enable | 0 | 1 | 0 | FREECOOL_DISABLE FREECOOL_ENABLE
20015 | FreecoolingAirFlow |  | % | 50 | 100 | 100
20016 | FreecoolingTempEU |  | °C (°F) | 12(53,6) | 25(77) | 20
20017 | FreecoolingOnMonth |  | Month for start freecooling season | 1 | 12 | 6
20018 | FreecoolingOnDay |  | Day for start freecooling season | 1 | 31 | 1
20019 | FreecoolingOnHour |  | Hour for start freecooling | 0 | 23 | 20
20020 | FreecoolingOnMin |  | Min for start freecooling | 0 | 59 | 0
20021 | FreecoolingOffMonth |  | Month for stop freecooling season | 1 | 12 | 9
20022 | FreecoolingOffDay |  | Day for stop freecooling season | 1 | 31 | 1
20023 | FreecoolingOffHour |  | Hour for stop freecooling | 0 | 23 | 6
20024 | FreecoolingOffmin |  | Min for stop freecooling | 0 | 59 | 0
20025 | PID_Postheater1_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20026 | PID_Postheater1_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20027 | PID_Postheater1_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20028 | PID_Postheater2_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20029 | PID_Postheater2_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20030 | PID_Postheater2_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20031 | PID_Peheater_Proportional range |  | PID_Pxx °C (°F) | 5(41) | 60(140) | 20(68)
20032 | PID_Preheater_Integration constant |  | PID_xIx (sec) | 1 | 255 | 60
20033 | PID_Preheater_derivative constant |  | PID_xxD (min) | 0 | 10 | 0
20034 | SupplyDuctTempMax |  | Maximal supply duct temperature °C (°F) | 25(77) | 45(113) | 30(86)
20035 | SupplyDuctTempMin |  | Minimal supply duct temperature °C (°F) | 15(59) | 20(68) | 15(59)
20036 | RequiredPressureVAV |  | Pa | 0 | 1000 | 30
20037 | BypassTemperature |  | Minimal bypass temperature | 0(32) | 20(68) | 15(59)
20038 | MaxFlowCalibration |  | Maximal flow after calibration | 0 | 15000 | dle adresy 10114 nebo 10111
20039 | MaxPressureCalibration |  | Maximal pressure after calibration | 0 | 5000 | 30
20040 | FanCalibrationProcessed |  | FanCalibrationSucessfullyTerminated | 0 | 1 | 0 | FAN_CALIBRATION_NONE FAN_CALIBRATION_PROCESSED
20041 | FilterCalibrationProcessed |  | FilterCalibrationSucessfullyTerminated | 0 | 1 | 0 | FILTER_CALIBRATION_NONE FILTER_CALIBRATION_PROCESSED
20042 | reserva |  |  | 0 | 0 | 0
20043 | reserva |  |  | 0 | 0 | 0
20044 | OutsideTempSensorBMS |  | Outside temerature from BMS enable | 0 | 1 | 0 | OUT_TEMP-BMS_ENABLE OUT_TEMP_BMS_DISABLE
20045 | FlowReductionUnderDuctMin |  | 0 - disable 1 - enable | 0 | 1 | 1 | DUCT_MIN_FLOW_REDUCTION_DISABLE DUCT_MIN_FLOW_REDUCTION_ENABLE
20046 | Rec_CO2Level1100 |  | 350 - 1100ppm | 350 | 1100 | 1000
20047 | Rec_CO2Level2000 |  | 350 - 2000ppm | 350 | 2000 | 1000
20048 | Rec_Temp_setpoint |  | °C (°F) | 25(77) | 40(104) | 30(86)
20049 | Rec_Temp_setpoint_winter |  | °C (°F) | -20(-4) | -5(23) | -10(14)
20050 | Rec_PID_P |  | PID_Pxx % | 5 | 70 | 20
20051 | Rec_PID_I |  | PID_xIx (sec) | 1 | 255 | 60
20052 | Rec_PID_D |  | PID_xxD (min) | 0 | 10 | 0
AIR CURTAIN
20053 | SummerHeatEnable |  | Enable summer heat blocation | 0 | 1 | 0
20054 | WinterMounthStart |  | Mounth when winter starts | 1 | 12 | 10
20055 | WinterMounthStop |  | Mounth when winter ends | 1 | 12 | 4
20056 | SummerTempHeaterEnable |  | Limit temperature to enable heat in summer | 10 | 20 | 15
20057 | AutoSpeedControlEnable |  | Enable automatic speed control use 0 - disable 1 - enable | 0 | 1 | 0
20058 | AutoSpeedControlDeltaT |  | Delta T for automatic speed control changes (setpoint vs outside temperature) | 1 | 5 | 1
20059 | NightTempReductionEnable |  | NightTempReductionEnable | 0 | 1 | 0
20060 | NightTempReductionSetpointShift |  | Temperature setpoint shift for night reduction | -1 | -5 | -3
20061 | NightStartHour |  | Definition when night time start (hour) | 0 | 23 | 0
20062 | NightStartMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20063 | NightStopHour |  | Definition when night time start (hour) | 0 | 23 | 0
20064 | NightStopMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20065 | DoorContactEnable |  | Door contact enable to use 0 - disable 1 - enable | 0 | 1 | 1
20066 | DoorContactMode |  | Door contact mode selection 0 - Fixed 1 - Selflearning | 0 | 1 | 0
20067 | DoorContactFixedFlow_open |  | Air flow in ‰ for Fixed door Range set according (FACTORY SET: 10102 and 10111 …10116) | - | - | 200
20068 | DoorContactFixedHeat_open |  | Heat output for fixed door | 0 | 100 | 0
20069 | DoorContactFixedTempSetpoint |  | Setpoint temperature for Fixed door Range set according selected sensor: Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20070 | DoorContactFixedOverRunEnable |  | Overrun mode 0 - disable 1 - time interval 2 - temperature | 0 | 2 | 1
20071 | DoorContactFixedOverRunMinflowTime |  | Overrun time on minimal speed 5 - 300sec | 5 | 300 | 10
20072 | DoorContactFixedOverRunMaxflowTime |  | Overrun time on maximal speed 5 - 300sec | 5 | 300 | 10
20073 | DoorContactFixedOverRunTempSetpoint |  | Setpoint temperature for overrun to temperature Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20074 | DoorContactFixedOverRunTempSelect |  | Overrun temperature sensor selection 0 - Sensor CT-ROOM 1 - Thermostat | 0 | 1 | 0

## Sammanställning
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
SERVICE
20053 | SummerHeatEnable |  | Enable summer heat blocation | 0 | 1 | 0
20054 | WinterMounthStart |  | Mounth when winter starts | 1 | 12 | 10
20055 | WinterMounthStop |  | Mounth when winter ends | 1 | 12 | 4
20056 | SummerTempHeaterEnable |  | Limit temperature to enable heat in summer | 10 | 20 | 15
20057 | AutoSpeedControlEnable |  | Enable automatic speed control use 0 - disable 1 - enable | 0 | 1 | 0
20058 | AutoSpeedControlDeltaT |  | Delta T for automatic speed control changes (setpoint vs outside temperature) | 1 | 5 | 1
20059 | NightTempReductionEnable |  | NightTempReductionEnable | 0 | 1 | 0
20060 | NightTempReductionSetpointShift |  | Temperature setpoint shift for night reduction | -1 | -5 | -3
20061 | NightStartHour |  | Definition when night time start (hour) | 0 | 23 | 0
20062 | NightStartMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20063 | NightStopHour |  | Definition when night time start (hour) | 0 | 23 | 0
20064 | NightStopMinute |  | Definition when night time ends (hour) | 0 | 59 | 0
20065 | DoorContactEnable |  | Door contact enable to use 0 - disable 1 - enable | 0 | 1 | 1
20066 | DoorContactMode |  | Door contact mode selection 0 - Fixed 1 - Selflearning | 0 | 1 | 0
20067 | DoorContactFixedFlow_open |  | Air flow in ‰ for Fixed door Range set according (FACTORY SET: 10102 and 10111 …10116) | - | - | 200
20068 | DoorContactFixedHeat_open |  | Heat output for fixed door | 0 | 100 | 0
20069 | DoorContactFixedTempSetpoint |  | Setpoint temperature for Fixed door Range set according selected sensor: Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20070 | DoorContactFixedOverRunEnable |  | Overrun mode 0 - disable 1 - time interval 2 - temperature | 0 | 2 | 1
20071 | DoorContactFixedOverRunMinflowTime |  | Overrun time on minimal speed 5 - 300sec | 5 | 300 | 10
20072 | DoorContactFixedOverRunMaxflowTime |  | Overrun time on maximal speed 5 - 300sec | 5 | 300 | 10
20073 | DoorContactFixedOverRunTempSetpoint |  | Setpoint temperature for overrun to temperature Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | - | 15
20074 | DoorContactFixedOverRunTempSelect |  | Overrun temperature sensor selection 0 - Sensor CT-ROOM 1 - Thermostat | 0 | 1 | 0
SERVICE HARD
25032 | OutsideTempSensorAirCurtain |  | Outside temerature from BMS enable | 0 | 2 | 0 | OUT_TEMP_DISABLE = 0, OUT_TEMP_EXT1, OUT_TEMP_BMS
25033 | TemperatureControlMode |  | 0 - manual 1 - automatic | 0 | 1 | 0
25034 | ErrorLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25035 | DoorContactLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25036 | ExtCtrlLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25037 | RoomThermLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25038 | ExtCtrlFunction |  | 0 - DI-5.x = NOT USED 1 - DI-5.x = External control 2 - DI-5.x = Night reduction | 0 | 2 | 0
25039 | AntifreezeTempAirSet |  | Antifreeze air temperature (INT-1) | 5 | 15 | 5
25040 | AntifreezeTempWoutSet |  | Antifreeze water return temperature | 10 | 20 | 10
25041 | AntifreezeTempDxSet |  | Antifreeze fluid temperature | 0 | 5 | 0
25042 | NumberOfSlaveUnit |  | Specified number of slave units | 0 | 10 | 0
25043 | GlobalDoorContactEnable |  | Door contact shared from master | 0 | 1 | 1
25044 | GlobalExtCtrlEnable |  | External control shared from master | 0 | 1 | 1
25045 | LocalSlavePowerSwitchEnable |  | 0 - disable 1 - enable | 0 | 1 | 0
25046 | PreferManualOutput |  | 0 - digital 1 - analog | 0 | 1 | 0
25047 | NumOfDigitalHeaters |  |  | 0 | 1 | 1
25048 | NumOfMotors |  |  | 0 | 8 | 0
SHARE
21024 | ACR_ManualHeat |  | Heater power for manual mode | 0 | 100 | 0
21025 | TimeSwHeat |  |  | 0 | 100 | 0
SlaveSwitchOn
21026 | bit0 |  | Slave1 - off/on | 0 | 1 | 0
| bit1 |  | Slave2 - off/on | 0 | 1 | 0
| bit2 |  | Slave3 - off/on | 0 | 1 | 0
| bit3 |  | Slave4 - off/on | 0 | 1 | 0
| bit4 |  | Slave5 - off/on | 0 | 1 | 0
| bit5 |  | Slave6 - off/on | 0 | 1 | 0
| bit6 |  | Slave7 - off/on | 0 | 1 | 0
| bit7 |  | Slave8 - off/on | 0 | 1 | 0
| bit8 |  | Slave9 - off/on | 0 | 1 | 0
| bit9 |  | Slave10 - off/on | 0 | 1 | 0
| bit10 |  | Slave11 - off/on | 0 | 1 | 0
| bit11 |  | Slave12 - off/on | 0 | 1 | 0
| bit12 |  | Slave13 - off/on | 0 | 1 | 0
| bit13 |  | Slave14 - off/on | 0 | 1 | 0
| bit14 |  | Slave15 - off/on | 0 | 1 | 0
| bit15 |  | Slave16 - off/on | 0 | 1 | 0
21027 | Temperature Night |  |  | 5 | 30 | 15
TIME DRIVER
17000 | SetYear |  |  | 2000 | 2100 | -
17001 | SetMonth |  |  | 1 | 12 | -
17002 | SetDay |  |  | 1 | 31 | -
17003 | SetDayOfWeek |  |  | 1 | 7 | -
17004 | SetHour |  |  | 0 | 23 | -
17005 | SetMin |  |  | 0 | 59 | -
17006 | SetSec |  |  | 0 | 59 | -
17007 | SetFlag |  |  | 0 | 1 | 0 |  | set time date to unit
17008 | ErrorLogNum |  |  | 1 | 20 | 1
17009 | ErrorLogClearFlag |  |  | 0 | 1 | 0
TIME SWITCH WEEK
Time_switch register (Factory reset set to default)
27000 | TimeSw_Monday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27001 | TimeSw_Monday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27002 | TimeSw_Monday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27003 | TimeSw_Monday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27004 | TimerSw_Monday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27005 | TimerSw_Monday_1_Heat |  | Only for AC | 0 | 100 | 0
27006 | TimeSw_Monday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27007 | TimeSw_Monday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27008 | TimeSw_Monday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27009 | TimeSw_Monday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27010 | TimerSw_Monday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27011 | TimerSw_Monday_2_Heat |  | Only for AC | 0 | 100 | 0
27012 | TimeSw_Monday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27013 | TimeSw_Monday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27014 | TimeSw_Monday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27015 | TimeSw_Monday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27016 | TimerSw_Monday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27017 | TimerSw_Monday_3_Heat |  | Only for AC | 0 | 100 | 0
27018 | TimeSw_Monday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27019 | TimeSw_Monday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27020 | TimeSw_Monday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27021 | TimeSw_Monday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27022 | TimerSw_Monday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27023 | TimerSw_Monday_4_Heat |  | Only for AC | 0 | 100 | 0
27024 | TimeSw_Monday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27025 | TimeSw_Monday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27026 | TimeSw_Monday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27027 | TimeSw_Monday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27028 | TimerSw_Monday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27029 | TimerSw_Monday_5_Heat |  | Only for AC | 0 | 100 | 0
27030 | TimeSw_Monday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27031 | TimeSw_Monday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27032 | TimeSw_Monday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27033 | TimeSw_Monday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27034 | TimerSw_Monday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27035 | TimerSw_Monday_6_Heat |  | Only for AC | 0 | 100 | 0
27036 | TimeSw_Monday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27037 | TimeSw_Monday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27038 | TimeSw_Monday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27039 | TimeSw_Monday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27040 | TimerSw_Monday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27041 | TimerSw_Monday_7_Heat |  | Only for AC | 0 | 100 | 0
27042 | TimeSw_Monday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27043 | TimeSw_Monday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27044 | TimeSw_Monday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27045 | TimeSw_Monday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27046 | TimerSw_Monday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27047 | TimerSw_Monday_8_Heat |  | Only for AC | 0 | 100 | 0
27048 | TimeSw_Tuesday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27049 | TimeSw_Tuesday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27050 | TimeSw_Tuesday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27051 | TimeSw_Tuesday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27052 | TimerSw_Tuesday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27053 | TimerSw_Tuesday_1_Heat |  | Only for AC | 0 | 100 | 0
27054 | TimeSw_Tuesday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27055 | TimeSw_Tuesday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27056 | TimeSw_Tuesday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27057 | TimeSw_Tuesday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27058 | TimerSw_Tuesday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27059 | TimerSw_Tuesday_2_Heat |  | Only for AC | 0 | 100 | 0
27060 | TimeSw_Tuesday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27061 | TimeSw_Tuesday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27062 | TimeSw_Tuesday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27063 | TimeSw_Tuesday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27064 | TimerSw_Tuesday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27065 | TimerSw_Tuesday_3_Heat |  | Only for AC | 0 | 100 | 0
27066 | TimeSw_Tuesday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27067 | TimeSw_Tuesday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27068 | TimeSw_Tuesday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27069 | TimeSw_Tuesday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27070 | TimerSw_Tuesday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27071 | TimerSw_Tuesday_4_Heat |  | Only for AC | 0 | 100 | 0
27072 | TimeSw_Tuesday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27073 | TimeSw_Tuesday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27074 | TimeSw_Tuesday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27075 | TimeSw_Tuesday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27076 | TimerSw_Tuesday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27077 | TimerSw_Tuesday_5_Heat |  | Only for AC | 0 | 100 | 0
27078 | TimeSw_Tuesday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27079 | TimeSw_Tuesday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27080 | TimeSw_Tuesday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27081 | TimeSw_Tuesday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27082 | TimerSw_Tuesday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27083 | TimerSw_Tuesday_6_Heat |  | Only for AC | 0 | 100 | 0
27084 | TimeSw_Tuesday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27085 | TimeSw_Tuesday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27086 | TimeSw_Tuesday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27087 | TimeSw_Tuesday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27088 | TimerSw_Tuesday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27089 | TimerSw_Tuesday_7_Heat |  | Only for AC | 0 | 100 | 0
27090 | TimeSw_Tuesday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27091 | TimeSw_Tuesday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27092 | TimeSw_Tuesday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27093 | TimeSw_Tuesday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27094 | TimerSw_Tuesday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27095 | TimerSw_Tuesday_8_Heat |  | Only for AC | 0 | 100 | 0
27096 | TimeSw_Wensday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27097 | TimeSw_Wensday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27098 | TimeSw_Wensday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27099 | TimeSw_Wensday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27100 | TimerSw_Wensday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27101 | TimerSw_Wensday_1_Heat |  | Only for AC | 0 | 100 | 0
27102 | TimeSw_Wensday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27103 | TimeSw_Wensday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27104 | TimeSw_Wensday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27105 | TimeSw_Wensday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27106 | TimerSw_Wensday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27107 | TimerSw_Wensday_2_Heat |  | Only for AC | 0 | 100 | 0
27108 | TimeSw_Wensday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27109 | TimeSw_Wensday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27110 | TimeSw_Wensday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27111 | TimeSw_Wensday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27112 | TimerSw_Wensday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27113 | TimerSw_Wensday_3_Heat |  | Only for AC | 0 | 100 | 0
27114 | TimeSw_Wensday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27115 | TimeSw_Wensday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27116 | TimeSw_Wensday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27117 | TimeSw_Wensday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27118 | TimerSw_Wensday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27119 | TimerSw_Wensday_4_Heat |  | Only for AC | 0 | 100 | 0
27120 | TimeSw_Wensday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27121 | TimeSw_Wensday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27122 | TimeSw_Wensday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27123 | TimeSw_Wensday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27124 | TimerSw_Wensday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27125 | TimerSw_Wensday_5_Heat |  | Only for AC | 0 | 100 | 0
27126 | TimeSw_Wensday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27127 | TimeSw_Wensday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27128 | TimeSw_Wensday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27129 | TimeSw_Wensday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27130 | TimerSw_Wensday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27131 | TimerSw_Wensday_6_Heat |  | Only for AC | 0 | 100 | 0
27132 | TimeSw_Wensday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27133 | TimeSw_Wensday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27134 | TimeSw_Wensday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27135 | TimeSw_Wensday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27136 | TimerSw_Wensday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27137 | TimerSw_Wensday_7_Heat |  | Only for AC | 0 | 100 | 0
27138 | TimeSw_Wensday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27139 | TimeSw_Wensday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27140 | TimeSw_Wensday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27141 | TimeSw_Wensday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27142 | TimerSw_Wensday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27143 | TimerSw_Wensday_8_Heat |  | Only for AC | 0 | 100 | 0
27144 | TimeSw_Thursday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27145 | TimeSw_Thursday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27146 | TimeSw_Thursday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27147 | TimeSw_Thursday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27148 | TimerSw_Thursday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27149 | TimerSw_Thursday_1_Heat |  | Only for AC | 0 | 100 | 0
27150 | TimeSw_Thursday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27151 | TimeSw_Thursday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27152 | TimeSw_Thursday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27153 | TimeSw_Thursday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27154 | TimerSw_Thursday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27155 | TimerSw_Thursday_2_Heat |  | Only for AC | 0 | 100 | 0
27156 | TimeSw_Thursday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27157 | TimeSw_Thursday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27158 | TimeSw_Thursday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27159 | TimeSw_Thursday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27160 | TimerSw_Thursday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27161 | TimerSw_Thursday_3_Heat |  | Only for AC | 0 | 100 | 0
27162 | TimeSw_Thursday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27163 | TimeSw_Thursday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27164 | TimeSw_Thursday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27165 | TimeSw_Thursday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27166 | TimerSw_Thursday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27167 | TimerSw_Thursday_4_Heat |  | Only for AC | 0 | 100 | 0
27168 | TimeSw_Thursday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27169 | TimeSw_Thursday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27170 | TimeSw_Thursday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27171 | TimeSw_Thursday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27172 | TimerSw_Thursday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27173 | TimerSw_Thursday_5_Heat |  | Only for AC | 0 | 100 | 0
27174 | TimeSw_Thursday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27175 | TimeSw_Thursday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27176 | TimeSw_Thursday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27177 | TimeSw_Thursday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27178 | TimerSw_Thursday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27179 | TimerSw_Thursday_6_Heat |  | Only for AC | 0 | 100 | 0
27180 | TimeSw_Thursday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27181 | TimeSw_Thursday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27182 | TimeSw_Thursday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27183 | TimeSw_Thursday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27184 | TimerSw_Thursday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27185 | TimerSw_Thursday_7_Heat |  | Only for AC | 0 | 100 | 0
27186 | TimeSw_Thursday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27187 | TimeSw_Thursday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27188 | TimeSw_Thursday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27189 | TimeSw_Thursday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27190 | TimerSw_Thursday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27191 | TimerSw_Thursday_8_Heat |  | Only for AC | 0 | 100 | 0
27192 | TimeSw_Friday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27193 | TimeSw_Friday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27194 | TimeSw_Friday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27195 | TimeSw_Friday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27196 | TimerSw_Friday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27197 | TimerSw_Friday_1_Heat |  | Only for AC | 0 | 100 | 0
27198 | TimeSw_Friday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27199 | TimeSw_Friday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27200 | TimeSw_Friday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27201 | TimeSw_Friday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27202 | TimerSw_Friday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27203 | TimerSw_Friday_2_Heat |  | Only for AC | 0 | 100 | 0
27204 | TimeSw_Friday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27205 | TimeSw_Friday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27206 | TimeSw_Friday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27207 | TimeSw_Friday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27208 | TimerSw_Friday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27209 | TimerSw_Friday_3_Heat |  | Only for AC | 0 | 100 | 0
27210 | TimeSw_Friday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27211 | TimeSw_Friday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27212 | TimeSw_Friday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27213 | TimeSw_Friday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27214 | TimerSw_Friday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27215 | TimerSw_Friday_4_Heat |  | Only for AC | 0 | 100 | 0
27216 | TimeSw_Friday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27217 | TimeSw_Friday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27218 | TimeSw_Friday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27219 | TimeSw_Friday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27220 | TimerSw_Friday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27221 | TimerSw_Friday_5_Heat |  | Only for AC | 0 | 100 | 0
27222 | TimeSw_Friday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27223 | TimeSw_Friday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27224 | TimeSw_Friday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27225 | TimeSw_Friday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27226 | TimerSw_Friday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27227 | TimerSw_Friday_6_Heat |  | Only for AC | 0 | 100 | 0
27228 | TimeSw_Friday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27229 | TimeSw_Friday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27230 | TimeSw_Friday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27231 | TimeSw_Friday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27232 | TimerSw_Friday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27233 | TimerSw_Friday_7_Heat |  | Only for AC | 0 | 100 | 0
27234 | TimeSw_Friday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27235 | TimeSw_Friday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27236 | TimeSw_Friday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27237 | TimeSw_Friday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27238 | TimerSw_Friday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27239 | TimerSw_Friday_8_Heat |  | Only for AC | 0 | 100 | 0
27240 | TimeSw_Saturday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27241 | TimeSw_Saturday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27242 | TimeSw_Saturday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27243 | TimeSw_Saturday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27244 | TimerSw_Saturday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27245 | TimerSw_Saturday_1_Heat |  | Only for AC | 0 | 100 | 0
27246 | TimeSw_Saturday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27247 | TimeSw_Saturday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27248 | TimeSw_Saturday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27249 | TimeSw_Saturday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27250 | TimerSw_Saturday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27251 | TimerSw_Saturday_2_Heat |  | Only for AC | 0 | 100 | 0
27252 | TimeSw_Saturday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27253 | TimeSw_Saturday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27254 | TimeSw_Saturday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27255 | TimeSw_Saturday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27256 | TimerSw_Saturday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27257 | TimerSw_Saturday_3_Heat |  | Only for AC | 0 | 100 | 0
27258 | TimeSw_Saturday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27259 | TimeSw_Saturday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27260 | TimeSw_Saturday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27261 | TimeSw_Saturday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27262 | TimerSw_Saturday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27263 | TimerSw_Saturday_4_Heat |  | Only for AC | 0 | 100 | 0
27264 | TimeSw_Saturday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27265 | TimeSw_Saturday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27266 | TimeSw_Saturday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27267 | TimeSw_Saturday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27268 | TimerSw_Saturday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27269 | TimerSw_Saturday_5_Heat |  | Only for AC | 0 | 100 | 0
27270 | TimeSw_Saturday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27271 | TimeSw_Saturday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27272 | TimeSw_Saturday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27273 | TimeSw_Saturday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27274 | TimerSw_Saturday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27275 | TimerSw_Saturday_6_Heat |  | Only for AC | 0 | 100 | 0
27276 | TimeSw_Saturday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27277 | TimeSw_Saturday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27278 | TimeSw_Saturday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27279 | TimeSw_Saturday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27280 | TimerSw_Saturday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27281 | TimerSw_Saturday_7_Heat |  | Only for AC | 0 | 100 | 0
27282 | TimeSw_Saturday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27283 | TimeSw_Saturday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27284 | TimeSw_Saturday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27285 | TimeSw_Saturday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27286 | TimerSw_Saturday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27287 | TimerSw_Saturday_8_Heat |  | Only for AC | 0 | 100 | 0
27288 | TimeSw_Sunday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27289 | TimeSw_Sunday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27290 | TimeSw_Sunday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27291 | TimeSw_Sunday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27292 | TimerSw_Sunday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27293 | TimerSw_Sunday_1_Heat |  | Only for AC | 0 | 100 | 0
27294 | TimeSw_Sunday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27295 | TimeSw_Sunday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27296 | TimeSw_Sunday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27297 | TimeSw_Sunday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27298 | TimerSw_Sunday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27299 | TimerSw_Sunday_2_Heat |  | Only for AC | 0 | 100 | 0
27300 | TimeSw_Sunday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27301 | TimeSw_Sunday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27302 | TimeSw_Sunday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27303 | TimeSw_Sunday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27304 | TimerSw_Sunday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27305 | TimerSw_Sunday_3_Heat |  | Only for AC | 0 | 100 | 0
27306 | TimeSw_Sunday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27307 | TimeSw_Sunday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27308 | TimeSw_Sunday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27309 | TimeSw_Sunday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27310 | TimerSw_Sunday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27311 | TimerSw_Sunday_4_Heat |  | Only for AC | 0 | 100 | 0
27312 | TimeSw_Sunday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27313 | TimeSw_Sunday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27314 | TimeSw_Sunday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27315 | TimeSw_Sunday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27316 | TimerSw_Sunday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27317 | TimerSw_Sunday_5_Heat |  | Only for AC | 0 | 100 | 0
27318 | TimeSw_Sunday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27319 | TimeSw_Sunday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27320 | TimeSw_Sunday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27321 | TimeSw_Sunday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27322 | TimerSw_Sunday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27323 | TimerSw_Sunday_6_Heat |  | Only for AC | 0 | 100 | 0
27324 | TimeSw_Sunday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27325 | TimeSw_Sunday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27326 | TimeSw_Sunday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27327 | TimeSw_Sunday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27328 | TimerSw_Sunday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27329 | TimerSw_Sunday_7_Heat |  | Only for AC | 0 | 100 | 0
27330 | TimeSw_Sunday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27331 | TimeSw_Sunday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27332 | TimeSw_Sunday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27333 | TimeSw_Sunday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27334 | TimerSw_Sunday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27335 | TimerSw_Sunday_8_Heat |  | Only for AC | 0 | 100 | 0
TIME SWITCH YEAR
Time_switch register (Factory reset set to default)
28000 | TimeSWYear_Enable |  | Time switch 1 Year enable | 0 | 1 | 1 | DISABLE ENABLE
28001 | TimeSwY_1_OnDay |  |  | 1 | 31 | 1
28002 | TimeSwY_1_OnMonth |  |  | 1 | 12 | 1
28003 | TimeSwY_1_OffDay |  |  | 1 | 31 | 1
28004 | TimeSwY_1_OffMonth |  |  | 1 | 31 | 1
28005 | TimeSwY_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28006 | TimeSwY_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28007 | TimeSwY_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28008 | TimeSwY_1_Heat |  | Only for AC | 0 | 100 | 0
28009 | TimeSwY_2_OnDay |  |  | 1 | 31 | 1
28010 | TimeSwY_2_OnMonth |  |  | 1 | 12 | 1
28011 | TimeSwY_2_OffDay |  |  | 1 | 31 | 1
28012 | TimeSwY_2_OffMonth |  |  | 1 | 31 | 1
28013 | TimeSwY_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28014 | TimeSwY_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28015 | TimeSwY_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28016 | TimeSwY_2_Heat |  | Only for AC | 0 | 100 | 0
28017 | TimeSwY_3_OnDay |  |  | 1 | 31 | 1
28018 | TimeSwY_3_OnMonth |  |  | 1 | 12 | 1
28019 | TimeSwY_3_OffDay |  |  | 1 | 31 | 1
28020 | TimeSwY_3_OffMonth |  |  | 1 | 31 | 1
28021 | TimeSwY_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28022 | TimeSwY_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28023 | TimeSwY_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28024 | TimeSwY_3_Heat |  | Only for AC | 0 | 100 | 0
28025 | TimeSwY_4_OnDay |  |  | 1 | 31 | 1
28026 | TimeSwY_4_OnMonth |  |  | 1 | 12 | 1
28027 | TimeSwY_4_OffDay |  |  | 1 | 31 | 1
28028 | TimeSwY_4_OffMonth |  |  | 1 | 31 | 1
28029 | TimeSwY_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28030 | TimeSwY_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28031 | TimeSwY_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28032 | TimeSwY_4_Heat |  | Only for AC | 0 | 100 | 0
28033 | TimeSwY_5_OnDay |  |  | 1 | 31 | 1
28034 | TimeSwY_5_OnMonth |  |  | 1 | 12 | 1
28035 | TimeSwY_5_OffDay |  |  | 1 | 31 | 1
28036 | TimeSwY_5_OffMonth |  |  | 1 | 31 | 1
28037 | TimeSwY_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28038 | TimeSwY_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28039 | TimeSwY_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28040 | TimeSwY_5_Heat |  | Only for AC | 0 | 100 | 0
28041 | TimeSwY_6_OnDay |  |  | 1 | 31 | 1
28042 | TimeSwY_6_OnMonth |  |  | 1 | 12 | 1
28043 | TimeSwY_6_OffDay |  |  | 1 | 31 | 1
28044 | TimeSwY_6_OffMonth |  |  | 1 | 31 | 1
28045 | TimeSwY_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28046 | TimeSwY_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28047 | TimeSwY_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28048 | TimeSwY_6_Heat |  | Only for AC | 0 | 100 | 0
28049 | TimeSwY_7_OnDay |  |  | 1 | 31 | 1
28050 | TimeSwY_7_OnMonth |  |  | 1 | 12 | 1
28051 | TimeSwY_7_OffDay |  |  | 1 | 31 | 1
28052 | TimeSwY_7_OffMonth |  |  | 1 | 31 | 1
28053 | TimeSwY_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28054 | TimeSwY_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28055 | TimeSwY_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28056 | TimeSwY_7_Heat |  | Only for AC | 0 | 100 | 0
28057 | TimeSwY_8_OnDay |  |  | 1 | 31 | 1
28058 | TimeSwY_8_OnMonth |  |  | 1 | 12 | 1
28059 | TimeSwY_8_OffDay |  |  | 1 | 31 | 1
28060 | TimeSwY_8_OffMonth |  |  | 1 | 31 | 1
28061 | TimeSwY_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28062 | TimeSwY_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28063 | TimeSwY_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28064 | TimeSwY_8_Heat |  | Only for AC | 0 | 100 | 0
28065 | TimeSwY_9_OnDay |  |  | 1 | 31 | 1
28066 | TimeSwY_9_OnMonth |  |  | 1 | 12 | 1
28067 | TimeSwY_9_OffDay |  |  | 1 | 31 | 1
28068 | TimeSwY_9_OffMonth |  |  | 1 | 31 | 1
28069 | TimeSwY_9_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28070 | TimeSwY_9_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28071 | TimeSwY_9_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28072 | TimeSwY_9_Heat |  | Only for AC | 0 | 100 | 0
28073 | TimeSwY_10_OnDay |  |  | 1 | 31 | 1
28074 | TimeSwY_10_OnMonth |  |  | 1 | 12 | 1
28075 | TimeSwY_10_OffDay |  |  | 1 | 31 | 1
28076 | TimeSwY_10_OffMonth |  |  | 1 | 31 | 1
28077 | TimeSwY_10_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28078 | TimeSwY_10_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28079 | TimeSwY_10_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28080 | TimeSwY_10_Heat |  | Only for AC | 0 | 100 | 0
NETWORK
Network register (Factory reset no effect)
26000 | IP adress 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
26001 | IP adress x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
26002 | IP adress x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
26003 | IP adress x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 1
26004 | Mask 0.x.x.x |  | Mask part1 (0x00-0xFF) | 0 | 255 | 255
26005 | Mask x.0.x.x |  | Mask part2 (0x00-0xFF) | 0 | 255 | 255
26006 | Mask x.x.0.x |  | Mask part3 (0x00-0xFF) | 0 | 255 | 255
26007 | Mask x.x.x.0 |  | Mask part4 (0x00-0xFF) | 0 | 255 | 0
26008 | Gateway 0.x.x.x |  | Gateway part1 (0x00-0xFF) | 0 | 255 | 192
26009 | Gateway x.0.x.x |  | Gateway part2 (0x00-0xFF) | 0 | 255 | 168
26010 | Gateway x.x.0.x |  | Gateway part3 (0x00-0xFF) | 0 | 255 | 0
26011 | Gateway x.x.x.0 |  | Gateway part4 (0x00-0xFF) | 0 | 255 | 0
26012 | DHCP |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
26013 | ModbusPort |  | Port number 1 - 0xFFFF | 1 | 0xFFFF | 502
NORDIC SERVICE
Nordic service register (Factory reset set to default)
43000 | Valve excercising enable |  |  | 0 | 1 | 0
43001 | Valve excercising time |  |  | 1 | 120 | 60
43002 | Valve bleeding |  |  | 0 | 30 | 0
43003 | Door close fan off enable |  |  | 0 | 1 | 0
43004 | Door close fan off temperature |  |  | 5 | 30 | 20
43005 | Door close fan off delay |  |  | 0 | 120
43006 | reserva |  |  | 0 | 0 | 0
43007 | Door fan limits open min |  |  | 15 | 40 | 20
43008 | Door fan limits open max |  |  | 40 | 100 | 100
43009 | Door fan limits close min |  |  | 15 | 40 | 20
43010 | Door fan limits close max |  |  | 40 | 100 | 100
43011 | Antifreze sensor enable |  |  | 0 | 3 | 3
| bit0 |  | Air | 0 | 1 | 1
| bit1 |  | Water | 0 | 1 | 1
43012 | Water return limit enable |  |  | 0 | 1 | 0
43013 | Water return limit temperature |  |  | 15 | 85 | 50
43014 | Outlet temp limit |  |  | 5 | 30 | 17
43015 | Alarm temp room enable |  |  | 0 | 1 | 0
43016 | Fan off temp room enable |  |  | 0 | 1 | 0
43017 | Fan off temp room |  |  | 1 | 5 | 2
43018 | Damper open |  |  | 0 | 100 | 10
43019 | Damper delay |  |  | 0 | 120 | 30
43020 | Savana fan limits min |  |  | 15 | 40 | 15
43021 | Savana fan limits max |  |  | 40 | 100 | 60
43022 | Outlet limitation room |  |  | 0 | 1
43023 | reserva |  |  | 0 | 0 | 0
43024 | reserva |  |  | 0 | 0 | 0
43025 | reserva |  |  | 0 | 0 | 0

## SERVICE HARD
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Service register (Factory reset no effect)
25000 | VentilationMode |  | 0 - Manual 1 - DCV 2 - CAV 3 - VAV 4 - VAVC4 5 - PCO | 0 | 5 | 0 | MANUAL DCV CAV VAV VAVC4
25001 | Water_antifreeze_outlet_fan |  | 0 - disable 1 - enable | 0 | 1 | 0 | WAOF_DISABLE WAOF_ENABLE
25002 | RecirculationMode |  | 0 - Disable 1 - Air Quality Sensor 2000 2 - Air Quality Sensor 1100 3 - Temperature | 0 | 3 | 0 | RECIRC_AQS RECIRC_TEMP
25003 | AQS sensor selection |  | 0 - non 1 - CO2 2000ppm 2 - CO2 1100ppm 3 - RH 4 - VOC 5 - External control 0 - 10V | 0 | 5 | 0 | AQS_NON AQS_CO2_2000 AQS_CO2_1100 AQS_RH AQS_VOC AQS_UNI_0_10V
25004 | ADB_external |  | 0 - disable 1 - enable | 0 | 1 | 0 | RECIRC_ENABLE RECIRC_DISABLE
25005 | Postheat_2_external |  | ALWAYS ANANLOG 0 - none (module B) 1 - electric 2 - water 3 - wco 4 - DX | 0 | 4 | 0 | NONE ELECTRIC WATER WCO DX
25006 | Recirculation_external |  | 0 - disable 1 - enable | 0 | 1 | 0 | RECIRC_ENABLE RECIRC_DISABLE
25007 | Preheater_2_external |  | ALWAYS ANALOG 0 - none 1 - electric 2 - water | 0 | 2 | 0 | PRE_NON PRE_ELECTRIC PRE_WATER
25008 | HwSettings |  | 0 - DI-4.x = FIRE 1 - DI-4.x = NONOCCUPIED | 0 | 1 | 1 | DI_4_1_FIRE DI_4_1_NOBODY
25009 | TempSensorSelection |  | 0 - Supply duct (15-45°C; 59-113F) 1 - Extract duct (15-30°C; 59-86F) 2 - Room (15-30°C; 59-86F) 3 - Thermostat 4 - Room BMS | 0 | 2 | 0 | T_SUPPLY_DUCT T_EXTRACT_DUCT T_ROOM
25010 | MinimalPowerDX |  | % | 10 | 100 | 40
25011 | DeadBandDX |  | mV | 100 | 2000 | 1000
25012 | MaxStartsPerHourDX |  | x-times/hour | 3 | 60 | 6
25013 | HeatCoolTimeOut |  | Heat/Cool timeout (min) | 1 | 20 | 3
25014 | DxControlSignal |  | 0 - 0-10V 1 - ON/OFF | 0 | 1 | 0 | DX_CTRL_SIGNAL_0_10V DX_CTRL_SIGNAL_ON_OFF
25015 | LogicDxErrorContact |  | 0 - connected = error 1 - connected = OK | 0 | 1 | 1 | DX_ERROR_CONNECTED DX_OK_ERROR_CONNECTED
25016 | LogicDxDefrost |  | 0 - connected = defrost 1 - connected = OK | 0 | 1 | 1 | DX_DEFROST_CONNECTED DX_OK_DEFROST_CONNECTED
25017 | LogicDxHeatCoolSwitch |  | 0 - connected = cooling 1 - connected = heating | 0 | 1 | 1 | DX_HEAT_CONNECTED DX_COOL_CONNECTED
25018 | LogicRunOutput |  | 0 - connected = stop 1 - connected = RUN | 0 | 1 | 0 | RUN_CONNECTED_STOP RUN_CONNECTED_RUN
25019 | FilterWoringHours |  | Filter working hours | 0 | 3000 | 0
25020 | FilterMaxHours |  | Maximal filter working hours | 200 | 3000 | 1440
25021 | modbus addres |  |  | 1 | 247 | 1
25022 | modbus baudrate |  | 4800 9600 14400 19200 38400 | 4800 | 38400 | 9600
25023 | modbus parity |  | NONE ODD EVEN | 0 | 2 | 1
25024 | AQS placement |  | MASTER SLAVE | 0 | 1 | 0
25025 | Slave present |  | 0 - non 1 - used | 0 | 1 | 0
25026 | PCO_dpress |  |  | -250 | 250 | 0
25027 | DCV_breating |  | 0 - non 1 - used | 0 | 1 | 0
25028 | HEPA_filter |  | 0 - non 1 - used | 0 | 1 | 0
25029 | Daylight_saving |  | 0 - NONE 1 - USED | 0 | 1 | 1
25030 | FireMode |  | FIRE_MODE_OFF FIRE_MODE_ALL_FAN FIRE_MODE_SUPPLY FIRE_MODE_RETURN | 0 | 3 | 2
25031 | FireFlow |  |  | 0 | 100
AIR CURTAIN
25032 | OutsideTempSensorAirCurtain |  | Outside temerature from BMS enable | 0 | 2 | 0 | OUT_TEMP_DISABLE = 0, OUT_TEMP_EXT1, OUT_TEMP_BMS
25033 | TemperatureControlMode |  | 0 - manual 1 - automatic | 0 | 1 | 0
25034 | ErrorLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25035 | DoorContactLogic |  | 0 - NC 1 - NO | 0 | 1 | 1
25036 | ExtCtrlLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25037 | RoomThermLogic |  | 0 - NC 1 - NO | 0 | 1 | 0
25038 | ExtCtrlFunction |  | 0 - DI-5.x = NOT USED 1 - DI-5.x = External control 2 - DI-5.x = Night reduction | 0 | 2 | 0
25039 | AntifreezeTempAirSet |  | Antifreeze air temperature (INT-1) | 5 | 15 | 5
25040 | AntifreezeTempWoutSet |  | Antifreeze water return temperature | 10 | 20 | 10
25041 | AntifreezeTempDxSet |  | Antifreeze fluid temperature | 0 | 5 | 0
25042 | NumberOfSlaveUnit |  | Specified number of slave units | 0 | 10 | 0
25043 | GlobalDoorContactEnable |  | Door contact shared from master | 0 | 1 | 1
25044 | GlobalExtCtrlEnable |  | External control shared from master | 0 | 1 | 1
25045 | LocalSlavePowerSwitchEnable |  | 0 - disable 1 - enable | 0 | 1 | 0
25046 | PreferManualOutput |  | 0 - digital 1 - analog | 0 | 1 | 0
25047 | NumOfDigitalHeaters |  |  | 0 | 1 | 1
25048 | NumOfMotors |  |  | 0 | 8 | 0
AHU
25049 | NumOfHeaterSection |  | 0 - 1 Section 1 - 2 Sections 2 - 3 Sections | 0 | 2 | 0
25050 | NumberOfSensors |  | IBUS Gateway | 0 | 24 | 0
25051 | modbus baudrate |  | IBUS Gateway | 0 | 4 | 0
25052 | modbus parity |  | IBUS Gateway | 0 | 2 | 1
25053 | Reserva1 |  |  | 0 | 0 | 0
25054 | Reserva2 |  |  | 0 | 0 | 0
25055 | IBUS Baudrate |  | 0 - 19200 1 - 9600 2 - 4800 | 0 | 2 | 0

## INFO
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Info register - read only (Factory reset no effect)
16000 | Jumper1 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16001 | Jumper2 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16002 | Jumper2 |  | 0 - non 1 - fitted | 0 | 1 | - | NON FITTED
16003 | ActualCurrent |  | mA | 0 | 0xFFFF | -
16004 | ActualVoltage |  | V | 0 | 0xFFFF | -
16005 | ActualPower |  | W | 0 | 0xFFFF | -
16006 | TotalConsumption_L |  | kW/h | 0 | 0xFFFF | -
16007 | TotalConsumption_H |  |  | 0 | 0xFFFF | -
16008 | IP adress 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
16009 | IP adress x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
16010 | IP adress x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
16011 | IP adress x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 100
16012 | Mask 0.x.x.x |  | Mask part1 (0x00-0xFF) | 0 | 255 | 255
16013 | Mask x.0.x.x |  | Mask part2 (0x00-0xFF) | 0 | 255 | 255
16014 | Mask x.x.0.x |  | Mask part3 (0x00-0xFF) | 0 | 255 | 255
16015 | Mask x.x.x.0 |  | Mask part4 (0x00-0xFF) | 0 | 255 | 0
16016 | Gateway 0.x.x.x |  | Gateway part1 (0x00-0xFF) | 0 | 255 | 192
16017 | Gateway x.0.x.x |  | Gateway part2 (0x00-0xFF) | 0 | 255 | 168
16018 | Gateway x.x.0.x |  | Gateway part3 (0x00-0xFF) | 0 | 255 | 0
16019 | Gateway x.x.x.0 |  | Gateway part4 (0x00-0xFF) | 0 | 255 | 1
16020 | DHCP |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0 | DHCP_OFF DHCP_ON
16021 | ModbusPort |  | Port number 1 - 0xFFFF | 1 | 0xFFFF | 502
16022 | MAC adress 0.x.x.x.x.x |  | MAC adress part1 | 0 | 255 | -
16023 | MAC adress x.0.x.x.x.x |  | MAC adress part2 | 0 | 255 | -
16024 | MAC adress x.x.0.x.x.x |  | MAC adress part3 | 0 | 255 | -
16025 | MAC adress x.x.x.0.x.x |  | MAC adress part4 | 0 | 255 | -
16026 | MAC adress x.x.x.x.0.x |  | MAC adress part5 | 0 | 255 | -
16027 | MAC adress x.x.x.x.x.0 |  | MAC adress part6 | 0 | 255 | -
16028 | HW version Module A |  |  | 0 | FFFF
16029 | FW Module A |  | Firmware version Module A | 0 | FFFF
16030 | FW Module B |  | Firmware version Module B | 0 | FFFF
16031 | FW Module C1 |  | Firmware version Module C1 | 0 | FFFF
16032 | FW Module C2 |  | Firmware version Module C2 | 0 | FFFF
16033 | FW Module C3 |  | Firmware version Module C3 | 0 | FFFF
16034 | FW Module C4 |  | Firmware version Module C4 | 0 | FFFF
16035 | FW Module C5 |  | Firmware version Module C5 | 0 | FFFF
16036 | FW Module C6 |  | Firmware version Module C6 | 0 | FFFF
16037 | FW Module C7 |  | Firmware version Module C7 | 0 | FFFF
16038 | FW Module C8 |  | Firmware version Module C8 | 0 | FFFF
16039 | FW Module C9 |  | Firmware version Module C9 | 0 | FFFF
16040 | FW Module C10 |  | Firmware version Module C10 | 0 | FFFF
16041 | FW Module G |  | Firmware version Module G | 0 | FFFF
16042 | Bootloader FW |  | Firmware version bootloader | 0 | FFFF
16043 | FW Module K |  | Firmware version Module K | 0 | FFFF
16044 | BTCP_1 |  | Firmware version bootloader CP | 0 | FFFF
16045 | FWCP_1 |  | Firmware version CP | 0 | FFFF
16046 | BTCP_2 |  | Firmware version bootloader CP | 0 | FFFF
16047 | FWCP_2 |  | Firmware version CP | 0 | FFFF
16048 | BTCP_3 |  | Firmware version bootloader CP | 0 | FFFF
16049 | FWCP_3 |  | Firmware version CP | 0 | FFFF
16050 | FW Module L1 |  | Firmware version Module L1 | 0 | FFFF
16051 | FW Module L2 |  | Firmware version Module L2 | 0 | FFFF
16052 | FW Module L3 |  | Firmware version Module L3 | 0 | FFFF
16053 | FW Module L4 |  | Firmware version Module L4 | 0 | FFFF
16054 | FW Module L5 |  | Firmware version Module L5 | 0 | FFFF
16055 | FW Module L6 |  | Firmware version Module L6 | 0 | FFFF
16056 | FW Module L7 |  | Firmware version Module L7 | 0 | FFFF
16057 | FW Module L8 |  | Firmware version Module L8 | 0 | FFFF
16058 | FW Module L9 |  | Firmware version Module L9 | 0 | FFFF
16059 | FW Module L10 |  | Firmware version Module L10 | 0 | FFFF
16060 | DHCP server |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
16061 | BACnet port |  |  | 1 | 0xFFFF | 0xBAC0
16062 | BACnet device ID MSB |  |  | 0 | 0xFFFF | 0
16063 | BACnet device ID LSB |  |  | 0 | 0xFFFF | 1
16064 | Local Broadcast 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
16065 | Local Broadcast x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
16066 | Local Broadcast x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
16067 | Local Broadcast x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 255
16068 | Relay error extend
16069 | App pin
Note on H6: Only with ModuleEnergyMeasure

## STATUS_AHU
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Unit global status1
15000 | bit0 |  | ON/OFF | 0 | 1 | ON OFF
| bit1 |  | MANUAL | 0 | 1 | MANUAL_NON MANUAL_MODE
| bit2 |  | CAV | 0 | 0 | CAV_NON CAV_MODE
| bit3 |  | VAV | 0 | 0 | VAV_NON VAV_MODE
| bit4 |  | DCV | 0 | 1 | DCV_NON DCV_MODE
| bit5 |  | Fire | 0 | 1 | FIRE_NON FIRE_MODE
| bit6 |  | Boost | 0 | 1 | BOOST_NON BOOST_MODE
| bit7 |  | Nobody (Nonoccupied) | 0 | 1 | NOBODY_NON NOBODY_MODE
| bit8 |  | Freecooling | 0 | 1 | FRCOOL_NON FRCOOL_MODE
| bit9 |  | Timeswitch | 0 | 1 | TIME_SW_NON TIME_SW_MODE
| bit10 |  | Calibration | 0 | 1 | CALIBR_NON CALIBR_MODE
| bit11 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit12 |  | DirectControl | 0 | 1 | DIR_CTRL_NON DIR_CTRL_MODE
| bit13 |  | FilterInfo | 0 | 1
| bit14 |  | FW update error | 0 | 1
| bit15 |  | FW update active | 0 | 1
Unit global status2
15001 | bit0 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit1 |  | WaterHeater waiting for hot water | 0 | 1 | HOT_WATER_NON HOT_WATER
| bit2 |  | WaterHeater waiting for supply air temperature | 0 | 1 | AIR_TEMP_NO_OK AIR_TEMP_OK
| bit3 |  | WCO searching inlet water temp (cold/hot) | 0 | 1 | WATER_CHECK_ON WATER_CHECK_OFF
| bit4 |  | Recirculation | 0 | 1 | RECIRCULATION NO_RECIRCULATION
| bit5 |  | Simulation | 0 | 1 | SIMULATION NO_SIMULATION
| bit6 |  | Prefreecooling | 0 | 1 | PREFREECOOLING NO_PREFREECOOLING
| bit7 |  | Temp Flow Reduction | 0 | 1
| bit8 |  | PassiveHouseRestriction | 0 | 1
| bit9 |  | AdbActive | 0 | 1
| bit10 |  | VAVC4 | 0 | 1
| bit11 |  | PCO | 0 | 1
Software error1
15002 | bit0 |  | SwFanInletError | 0 | 1
| bit1 |  | SwFanOutletError | 0 | 1
| bit2 |  | SwFilterInletError | 0 | 1
| bit3 |  | SwFilterOutletError | 0 | 1
| bit4 |  | SwFilterInletWarning | 0 | 1
| bit5 |  | SwFilterOutletWarning | 0 | 1
| bit6 |  | SwPreheater1Error | 0 | 1
| bit7 |  | SwPostheater1Error | 0 | 1
| bit8 |  | SwPostheater2Error | 0 | 1
| bit9 |  | SwPreheater2Error | 0 | 1
| bit10 |  | SwAQS SensorError | 0 | 1
| bit11 |  | SwRotaryWheelError | 0 | 1
| bit12 |  | SwADBError | 0 | 1
| bit13 |  | SwDXError | 0 | 1
| bit14 |  | SwDXDefrost | 0 | 1
| bit15 |  | SwCondensateDrain | 0 | 1
Software error2
15003 | bit0 |  | SwGError | 0 | 1
| bit1 |  | SwGlobalError | 0 | 1
| bit2 |  | SwKError | 0 | 1
| bit3 |  | FilterInfo | 0 | 1
| bit4 |  | CfgFileError | 0 | 1
| bit5 |  | SwFilterHepaError | 0 | 1
| bit6 |  | SwFilterHepaWarning | 0 | 1
| bit7 |  | IBUSGatewayError | 0 | 1
Sensor status1
15004 | bit0 |  | TempEXT1St | 0 | 1 | OK ERROR
| bit1 |  | TempEXT2St | 0 | 1 | OK ERROR
| bit2 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit3 |  | TempEXT4St (module B) | 0 | 0 | OK ERROR
| bit4 |  | TempINT0St (module B) | 0 | 0 | OK ERROR
| bit5 |  | TempINT1St | 0 | 1 | OK ERROR
| bit6 |  | TempINT2St | 0 | 1 | OK ERROR
| bit7 |  | TempWInSt (module B) | 0 | 0 | OK ERROR
| bit8 |  | TempWOutSt (module B) | 0 | 0 | OK ERROR
| bit9 |  | TempRoomSt | 0 | 1 | OK ERROR
| bit10 |  | SensorFilterInSt | 0 | 0 | OK ERROR
| bit11 |  | SensorFilterOutSt | 0 | 0 | OK ERROR
| bit12 |  | SensorFanInletSt | 0 | 0 | OK ERROR
| bit13 |  | SensorFanOutSt | 0 | 0 | OK ERROR
| bit14 |  | SensorPressSt | 0 | 0 | OK ERROR
| bit15 |  | SensorFlowAlaramSt | 0 | 0 | OK ERROR
Sensor status2
15005 | bit0 |  | AqsSensorSt | 0 | 0 | OK ERROR
| bit1 |  | SensorRHRecSt | 0 | 0 | OK ERROR
| bit2 |  | OutsideTempSensorBmsSt | 0 | 0 | OK ERROR
| bit3 |  | SensorRHSt | 0 | 0 | OK ERROR
| bit4 |  | Sensor Filter Hepa
Input Status1
15006 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | OK ERROR
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | OK ERROR
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Nobody (FIRE optional) | 0 | 1 | OK ERROR
| bit4 |  | Status DI_5_Boost | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_2 (Rotary wheel error) | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit13 |  | Status_DI_6_ADB_DX_error (module B) | 0 | 1 | OK ERROR
| bit14 |  | Status_DI_7_HeatPumpDefrost (module B) | 0 | 1 | OK ERROR
| bit15 |  | Status_DI_8_HeatPumpError (module B) | 0 | 1 | OK ERROR
Input Status2
15007 | bit0 |  | Status_DI_9_FIRE (module B) | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_10_CondensDrain (module B) | 0 | 1 | OK ERROR
Output Status1
15008 | bit0 |  | Status_DO_1_Flap_inlet | 0 | 1 | FLAP_CLOSED FLAP_OPEN
| bit1 |  | Status_DO_2_Flap_outlet | 0 | 1 | FLAP_CLOSED FLAP_OPEN
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | RUN_INDICATION NO_RUN
| bit3 |  | Status_DO_4_Water_pump | 0 | 1 | W_PUMP_A_ON W_PUMP_A_OFF
| bit4 |  | Status_DO_5_Heat_cool(module B) | 0 | 1 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Status_DO_6_Error | 0 | 1 | ERROR_B_OK ERROR_B_ERROR
| bit6 |  | Status_DO_7_ADB_on_off (module B) | 0 | 1 | ADB_ON ADB_OFF
| bit7 |  | Status_DO_8_HeatPump_on_off (module B) | 0 | 1 | HEAT_PUMP_ON HEAT_PUMP_OFF
| bit8 |  | Status_DO_9_WaterPump_on_off (module B) | 0 | 1 | W_PUMP_B_ON W_PUMP_B_OFF
Hardware Status1
15009 | bit0 |  | FRAM | 0 | 1
| bit1 |  | EEPROM | 0 | 1 | OK ERROR
| bit2 |  | Ethernet | 0 | 1 | OK ERROR
| bit3 |  | RTC_Cell | 0 | 1 | OK ERROR
| bit4 |  | MainPower | 0 | 1 | OK ERROR
| bit5 |  | ControlPanel | 0 | 1 | OK ERROR
| bit6 |  | B_module | 0 | 1 | OK ERROR
| bit7 |  | C_module_In_Press | 0 | 1 | OK ERROR
| bit8 |  | C_module_Out_Press | 0 | 1 | OK ERROR
| bit9 |  | C_module_In_Filter_Press | 0 | 1 | OK ERROR
| bit10 |  | C_module_Out_Filter_Press | 0 | 1 | OK ERROR
| bit11 |  | C_module_Duct_Press | 0 | 1 | OK ERROR
| bit12 |  | C_module_C4_Duct_Press | 0 | 1 | OK ERROR
| bit13 |  | C_module_RH | 0 | 1 | OK ERROR
| bit14 |  | AQS | 0 | 1 | OK ERROR
| bit15 |  | USB_over_current | 0 | 1 | OK ERROR
Hardware Status2
15010 | bit0 |  | Ethernet_communication | 0 | 1 | OK ERROR
| bit1 |  | C_module_Hepa_Press | 0 | 1 | OK ERROR
15011 | AirFlowInletFanDemand |  | m3/h (cfm) | 0 | 0xffff
15012 | AirFlowOutletFanDemand |  | m3/h (cfm) | 0 | 0xffff
15013 | AirFlowInletFanManual |  | ‰ of fan power | 0 | 1000
15014 | AirFlowOutletFanManual |  | ‰ of fan power | 0 | 1000
15015 | AirFlowInletFan |  | m3/h (cfm) | 0 | 0xffff
15016 | AirFlowOutletFan |  | m3/h (cfm) | 0 | 0xffff
15017 | TempEXT1 |  | °C (°F) | -40 (-40) | 100 (212)
15018 | TempEXT2 |  | °C (°F) | -40 (-40) | 100 (212)
15019 | TempEXT3 |  | °C (°F) | -40 (-40) | 100 (212)
15020 | TempEXT4 |  | °C (°F) (module B) | -40 (-40) | 100 (212)
15021 | TempINT0 |  | °C (°F) (module B) | -40 (-40) | 100 (212)
15022 | TempINT1 |  | °C (°F) | -40 (-40) | 100 (212)
15023 | TempINT2 |  | °C (°F) | -40 (-40) | 100 (212)
15024 | TempWIn |  | °C (°F) (module B) | -40 (-40) | 100 (212)
15025 | TempWOut |  | °C (°F) (module B) | -40 (-40) | 100 (212)
15026 | TempRoom |  | °C (°F) | -40 (-40) | 100 (212)
15027 | SensorFilterIn |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15028 | SensorFilterOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15029 | SensorFanInlet |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15030 | SensorFanOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15031 | SensorPress |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15032 | SensorFlowAlarm |  |  | 0 | 1
15033 | AqsSensorValue |  | % | 0 | 100
15034 | SensorRHRec |  | % | 0 | 100
15035 | SensorRH |  | % (module C) | 0 | 100
15036 | PowerPreheater1 |  | % | 0 | 100
15037 | PowerPreheater2 |  | % (module B) | 0 | 100
15038 | PowerPostheater1 |  | % | 0 | 100
15039 | PowerPostheater2 |  | % (module B) | 0 | 100
15040 | PowerPostheater3 |  | % (module B) | 0 | 100
15041 | BypassPossition |  | % | 0 | 100
15042 | Recirculation |  | % (module B) | 0 | 100
15043 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212)
15044 | InletFilterPercent |  | % | 0 | 100
15045 | OutletFilterPercent |  | % | 0 | 100
15046 | dummy |  |  | 0 | 0xFFFF
15047 | SensorFilterhEPA |  | Pa (in H2O) | 0 (0) | 2000 (8,029)
15048 | HepaFilterPercent |  | % | 0 | 100

## STATUS_AC
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Unit global status
18000 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Automatic heat | 0 | 1 | AUTOHEAT_NON AUTOHEAT_MODE
| bit2 |  | Automatic flow | 0 | 1 | AUTOFLOW_NON AUTOFLOW_MODE
| bit3 |  | NightReduction | 0 | 1 | NIGHTREDUCTION_NON NIGHTREDUCTION_MODE
| bit4 |  | Timeswitch | 0 | 1 | TIME_SW_NON TIME_SW_MODE
| bit5 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit6 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit7 |  | WaterHeater waiting for hot water | 0 | 1 | HOT_WATER_NON HOT_WATER
| bit8 |  | SummerHeat | 0 | 1 | WINTER SUMMER
| bit9 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit10 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit11 |  | Heater Under Power | 0 | 1
| bit12 |  | Savana Day Night | 0 | 1 | SAVANA_DAY SAVANA_NIGHT
| bit13 |  | reserva | 0 | 0
| bit14 |  | FW update error | 0 | 1
| bit15 |  | FW update active | 0 | 1
Software error
18001 | bit0 |  | SwFanError | 0 | 1
| bit1 |  | SwFanError1 | 0 | 1
| bit2 |  | SwFilterError | 0 | 1
| bit3 |  | SwFilterWarning | 0 | 1
| bit4 |  | SwHeaterError | 0 | 1
| bit5 |  | SwDXError | 0 | 1
| bit6 |  | SwDXDefrost | 0 | 1
| bit7 |  | SwGlobalError | 0 | 1
| bit8 |  | CfgFileError | 0 | 1
| bit9 |  | IBUSGatewayError | 0 | 1
| bit10 |  | Alarm temp room | 0 | 1
Software error 1
18002 | reserva
Sensor status
18003 | bit0 |  | TempEXT1St - Outside air | 0 | 1 | OK ERROR
| bit1 |  | TempEXT3St - Outlet air | 0 | 1 | OK ERROR
| bit2 |  | TempINT1St - Inlet air | 0 | 1 | OK ERROR
| bit3 |  | TempWOutSt - Water return | 0 | 1 | OK ERROR
| bit4 |  | TempRoomSt - Room | 0 | 1 | OK ERROR
| bit5 |  | OutsideTempSensorBmsSt | 0 | 1 | OK ERROR
| bit6 |  | RoomTempSensorBmsSt | 0 | 1 | OK ERROR
| bit7 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
Input Status
18004 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | OK ERROR
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | OK ERROR
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_RoomThermostat | 0 | 1 | OK ERROR
| bit4 |  | Status DI_5_Door | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit13 |  | Status_DI_6_ADB_DX_error | 0 | 1 | OK ERROR
| bit14 |  | Status_DI_7_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit15 |  | Status_DI_8_HeatPumpError | 0 | 1 | OK ERROR
Output Status
18005 | bit0 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit1 |  | Status_DO_1_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | RUN_INDICATION NO_RUN
| bit3 |  | Status_DO_4_Error | 0 | 1 | ERROR_INDICATION NO_ERROR
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Status_DO_6_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit6 |  | Damper | 0 | 1
18006 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
18007 | TempEXT1 - Outside air |  | °C (°F) | -40 (-40) | 100 (212)
18008 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
18009 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
18010 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
18011 | TempRoom - Room |  | °C (°F) | -40 (-40) | 100 (212)
18012 | SensorFlowAlarm |  |  | 0 | 1
18013 | PowerHeater |  | % | 0 | 100
18014 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212)
18015 | RoomBMS |  | °C (°F) | -40 (-40) | 101 (212)
18016 | FilterPercent |  | % | 0 | 100
18017 | dummy |  |  | 0 | 0xFFFF
Tacho Board Status
18018 | bit1 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit9 |  | Status_DI_TACHO_9 | 0 | 1 | OK ERROR
| bit10 |  | Status_DI_TACHO_10 | 0 | 1 | OK ERROR
18019 | Temperature Setpoint |  | Control Panel Temp setpoint | 0 | 1
18020 | Reserva

## SLAVE_AC_STATUS
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
Slave 1
Unit global status
14000 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat | 0 | 1
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14001 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14002 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14003 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14004 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14005 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14006 | SensorFlowAlarm |  |  | 0 | 1
14007 | PowerHeater |  | % | 0 | 100
Tacho Board
14008 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14009 | Reserva 2
Slave 2
Unit global status
14010 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14011 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14012 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14013 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14014 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14015 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14016 | SensorFlowAlarm |  |  | 0 | 1
14017 | PowerHeater |  | % | 0 | 100
Tacho Board
140018 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
140019 | Reserva 2
Slave 3
Unit global status
14020 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14021 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14022 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14023 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14024 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14025 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14026 | SensorFlowAlarm |  |  | 0 | 1
14027 | PowerHeater |  | % | 0 | 100
Tacho Board
14028 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14029 | Reserva 2
Slave 4
Unit global status
14030 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14031 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14032 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14033 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14034 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14035 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14036 | SensorFlowAlarm |  |  | 0 | 1
14037 | PowerHeater |  | % | 0 | 100
Tacho Board
14038 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14039 | Reserva 2
Slave 5
Unit global status
14040 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14041 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14042 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14043 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14044 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14045 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14046 | SensorFlowAlarm |  |  | 0 | 1
14047 | PowerHeater |  | % | 0 | 100
Tacho Board
14048 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14049 | Reserva 2
Slave 6
Unit global status
14050 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14051 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14052 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14053 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14054 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14055 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14056 | SensorFlowAlarm |  |  | 0 | 1
14057 | PowerHeater |  | % | 0 | 100
Tacho Board
14058 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14059 | Reserva 2
Slave 7
Unit global status
14060 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14061 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14062 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14063 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14064 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14065 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14066 | SensorFlowAlarm |  |  | 0 | 1
14067 | PowerHeater |  | % | 0 | 100
Tacho Board
14068 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14069 | Reserva 2
Slave 8
Unit global status
14070 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14071 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14072 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14073 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14074 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14075 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14076 | SensorFlowAlarm |  |  | 0 | 1
14077 | PowerHeater |  | % | 0 | 100
Tacho Board
14078 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14079 | Reserva 2
Slave 9
Unit global status
14080 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14081 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14082 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14083 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14084 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14085 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14086 | SensorFlowAlarm |  |  | 0 | 1
14087 | PowerHeater |  | % | 0 | 100
Tacho Board
14088 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14089 | Reserva 2
Slave 10
Unit global status
14090 | bit0 |  | OFF/ON | 0 | 1 | OFF ON
| bit1 |  | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 |  | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 |  | Heater Overheat
| bit4 |  | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 |  | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 |  | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 |  | TempEXT3St | 0 | 1 | OK ERROR
| bit8 |  | TempINT1St | 0 | 1 | OK ERROR
| bit9 |  | TempWOutSt | 0 | 1 | OK ERROR
| bit10 |  | SwFanError | 0 | 1
| bit11 |  | SwHeaterError | 0 | 1
| bit12 |  | SwDXError | 0 | 1
| bit13 |  | SwDXDefrost | 0 | 1
| bit14 |  | SwGlobalError | 0 | 1
| bit15 |  | Communication Error | 0 | 1
IO Status
14091 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 |  | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 |  | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 |  | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_5_ADB_DX_error | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_6_HeatPumpDefrost | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_7_HeatPumpError | 0 | 1 | OK ERROR
| bit8 |  | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 |  | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 |  | HeaterUnderPower
14092 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000 | ‰ of fan power
14093 | TempEXT3 - Outlet air |  | °C (°F) | -40 (-40) | 100 (212)
14094 | TempINT1 - Inlet air |  | °C (°F) | -40 (-40) | 100 (212)
14095 | TempWOut - Water return |  | °C (°F) | -40 (-40) | 100 (212)
14096 | SensorFlowAlarm |  |  | 0 | 1
14097 | PowerHeater |  | % | 0 | 100
Tacho Board
14098 | bit0 |  | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit1 |  | Status_DI_TACHO_2 | 0 | 1 | OK ERROR
| bit2 |  | Status_DI_TACHO_3 | 0 | 1 | OK ERROR
| bit3 |  | Status_DI_TACHO_4 | 0 | 1 | OK ERROR
| bit4 |  | Status_DI_TACHO_5 | 0 | 1 | OK ERROR
| bit5 |  | Status_DI_TACHO_6 | 0 | 1 | OK ERROR
| bit6 |  | Status_DI_TACHO_7 | 0 | 1 | OK ERROR
| bit7 |  | Status_DI_TACHO_8 | 0 | 1 | OK ERROR
| bit8 |  | Status_DI_TACHO_9 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 |  | Status_DI_TACHO_10 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
14099 | Reserva 2

## SHARE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Share register (Factory reset set to default)
21000 | Language |  | Language selection | 0 | 10 | 0 | ENGLISH - 0 FRENCH - 1 GERMAN - 2 RUSSIAN - 3 CZECH - 4 SPANISH - 5 PORTUGUESE - 6 ITALIAN - 7 SVENSKA - 8 SUOMI - 9
21001 | SwitchON |  | ON/OFF unit mode | 0 | 1 | 0 | OFF ON
21002 | AirFlowManual |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | - | -
21003 | Temperature |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE_HARD:25009): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-86F) Room (15-30°C; 59-86F) | - | - | -
21004 | TimeSwGlobalEnable |  | TimeSwitchGlobal enable/disable | 0 | 1 | 0 | TIMER_GLOBAL_DISABLE TIMER_GLOBAL_ENABLE
21005 | TimeSwMode |  | Active/Inactive timer mode (only read) | 0 | 1 | 0 | TIMER_MODE_OFF TIMER_MODE_ON
21006 | TimeSwFlow |  | only read
21007 | TimeSwTemp |  | only read
21008 | TimeSwOnOFF |  |  | 0 | 1 | 0 | TIMER_MODE_OFF TIMER_MODE_ON
21009 | BoostMode |  | Activation of Boost mode | 0 | 1 | 0 | BOOST_OFF BOOST_ON
21010 | NoBodyMode |  | Nobody mode (Nonoccupied) activation/deactivation | 0 | 1 | 0 | NOBODY_OFF NOBOBY_ON
21011 | FreecoolingMode |  | Freecooling activation/deactivation | 0 | 1 | 0 | FREECOOL_OFF FREECOOL_ON
21012 | FanCalibration |  | FanCalibrationStart | 0 | 1 | 0 | FAN_CAL_OFF FAN_CAL_ON
21013 | FilterCalibration |  | FilterCalibrationStart | 0 | 1 | 0 | FIL_CAL_OFF FIL_CAL_ON
21014 | DirectControlMode |  | DirectControlMode activation | 0 | 1 | 0 | DIR_CTRL_ON DIR_CTRL_OFF
21015 | Recirculation |  | Recirculation enable | 0 | 1 | 0 | RECIRCL_OFF RECIRCL_ON
21016 | FilterClogedTimerReset |  | 0 - count 1 - timer reset | 0 | 1 | 0 | FILTER_TIMER_COUNT FILTER-TIMER_RESET
21017 | Pin1 |  | Setting data for CP only | 0 | 9 | 1
21018 | Pin2 |  | Setting data for CP only | 0 | 9 | 2
21019 | Pin3 |  | Setting data for CP only | 0 | 9 | 3
21020 | Pin4 |  | Setting data for CP only | 0 | 9 | 4
21021 | Pin_mode |  | Setting data for CP only | 0 | 1 | 0
21022 | CP_refresh_flag |  | Setting data for CP only | 0 | 1 | 1
21023 | Backlight_set |  | % Setting data for CP only | 40 | 100 | 100
AIR CURTAIN
21024 | ACR_ManualHeat |  | Heater power for manual mode | 0 | 100 | 0
21025 | TimeSwHeat |  |  | 0 | 100 | 0
SlaveSwitchOn
21026 | bit0 |  | Slave1 - off/on | 0 | 1 | 0
| bit1 |  | Slave2 - off/on | 0 | 1 | 0
| bit2 |  | Slave3 - off/on | 0 | 1 | 0
| bit3 |  | Slave4 - off/on | 0 | 1 | 0
| bit4 |  | Slave5 - off/on | 0 | 1 | 0
| bit5 |  | Slave6 - off/on | 0 | 1 | 0
| bit6 |  | Slave7 - off/on | 0 | 1 | 0
| bit7 |  | Slave8 - off/on | 0 | 1 | 0
| bit8 |  | Slave9 - off/on | 0 | 1 | 0
| bit9 |  | Slave10 - off/on | 0 | 1 | 0
| bit10 |  | Slave11 - off/on | 0 | 1 | 0
| bit11 |  | Slave12 - off/on | 0 | 1 | 0
| bit12 |  | Slave13 - off/on | 0 | 1 | 0
| bit13 |  | Slave14 - off/on | 0 | 1 | 0
| bit14 |  | Slave15 - off/on | 0 | 1 | 0
| bit15 |  | Slave16 - off/on | 0 | 1 | 0
21027 | Temperature Night |  |  | 5 | 30 | 15

## TIME
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time register (Factory reset set to default)
17000 | ActualYear |  |  | 2000 | 2100
17001 | ActualMonth |  |  | 1 | 12
17002 | ActualDay |  |  | 1 | 31
17003 | ActualDayOfWeek |  |  | 1 | 7
17004 | ActualHour |  |  | 0 | 23
17005 | ActualMin |  |  | 0 | 59
17006 | ActualSec |  |  | 0 | 59

## TIME_DRIVER
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_driver register (Factory reset set to default)
17000 | SetYear |  |  | 2000 | 2100 | -
17001 | SetMonth |  |  | 1 | 12 | -
17002 | SetDay |  |  | 1 | 31 | -
17003 | SetDayOfWeek |  |  | 1 | 7 | -
17004 | SetHour |  |  | 0 | 23 | -
17005 | SetMin |  |  | 0 | 59 | -
17006 | SetSec |  |  | 0 | 59 | -
17007 | SetFlag |  |  | 0 | 1 | 0 |  | set time date to unit
17008 | ErrorLogNum |  |  | 1 | 20 | 1
17009 | ErrorLogClearFlag |  |  | 0 | 1 | 0

## TIME_SWITCH_WEEK
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_switch register (Factory reset set to default)
27000 | TimeSw_Monday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27001 | TimeSw_Monday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27002 | TimeSw_Monday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27003 | TimeSw_Monday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27004 | TimerSw_Monday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27005 | TimerSw_Monday_1_Heat |  | Only for AC | 0 | 100 | 0
27006 | TimeSw_Monday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27007 | TimeSw_Monday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27008 | TimeSw_Monday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27009 | TimeSw_Monday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27010 | TimerSw_Monday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27011 | TimerSw_Monday_2_Heat |  | Only for AC | 0 | 100 | 0
27012 | TimeSw_Monday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27013 | TimeSw_Monday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27014 | TimeSw_Monday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27015 | TimeSw_Monday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27016 | TimerSw_Monday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27017 | TimerSw_Monday_3_Heat |  | Only for AC | 0 | 100 | 0
27018 | TimeSw_Monday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27019 | TimeSw_Monday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27020 | TimeSw_Monday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27021 | TimeSw_Monday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27022 | TimerSw_Monday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27023 | TimerSw_Monday_4_Heat |  | Only for AC | 0 | 100 | 0
27024 | TimeSw_Monday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27025 | TimeSw_Monday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27026 | TimeSw_Monday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27027 | TimeSw_Monday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27028 | TimerSw_Monday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27029 | TimerSw_Monday_5_Heat |  | Only for AC | 0 | 100 | 0
27030 | TimeSw_Monday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27031 | TimeSw_Monday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27032 | TimeSw_Monday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27033 | TimeSw_Monday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27034 | TimerSw_Monday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27035 | TimerSw_Monday_6_Heat |  | Only for AC | 0 | 100 | 0
27036 | TimeSw_Monday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27037 | TimeSw_Monday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27038 | TimeSw_Monday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27039 | TimeSw_Monday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27040 | TimerSw_Monday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27041 | TimerSw_Monday_7_Heat |  | Only for AC | 0 | 100 | 0
27042 | TimeSw_Monday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27043 | TimeSw_Monday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27044 | TimeSw_Monday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27045 | TimeSw_Monday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27046 | TimerSw_Monday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27047 | TimerSw_Monday_8_Heat |  | Only for AC | 0 | 100 | 0
27048 | TimeSw_Tuesday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27049 | TimeSw_Tuesday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27050 | TimeSw_Tuesday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27051 | TimeSw_Tuesday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27052 | TimerSw_Tuesday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27053 | TimerSw_Tuesday_1_Heat |  | Only for AC | 0 | 100 | 0
27054 | TimeSw_Tuesday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27055 | TimeSw_Tuesday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27056 | TimeSw_Tuesday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27057 | TimeSw_Tuesday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27058 | TimerSw_Tuesday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27059 | TimerSw_Tuesday_2_Heat |  | Only for AC | 0 | 100 | 0
27060 | TimeSw_Tuesday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27061 | TimeSw_Tuesday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27062 | TimeSw_Tuesday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27063 | TimeSw_Tuesday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27064 | TimerSw_Tuesday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27065 | TimerSw_Tuesday_3_Heat |  | Only for AC | 0 | 100 | 0
27066 | TimeSw_Tuesday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27067 | TimeSw_Tuesday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27068 | TimeSw_Tuesday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27069 | TimeSw_Tuesday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27070 | TimerSw_Tuesday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27071 | TimerSw_Tuesday_4_Heat |  | Only for AC | 0 | 100 | 0
27072 | TimeSw_Tuesday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27073 | TimeSw_Tuesday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27074 | TimeSw_Tuesday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27075 | TimeSw_Tuesday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27076 | TimerSw_Tuesday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27077 | TimerSw_Tuesday_5_Heat |  | Only for AC | 0 | 100 | 0
27078 | TimeSw_Tuesday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27079 | TimeSw_Tuesday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27080 | TimeSw_Tuesday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27081 | TimeSw_Tuesday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27082 | TimerSw_Tuesday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27083 | TimerSw_Tuesday_6_Heat |  | Only for AC | 0 | 100 | 0
27084 | TimeSw_Tuesday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27085 | TimeSw_Tuesday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27086 | TimeSw_Tuesday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27087 | TimeSw_Tuesday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27088 | TimerSw_Tuesday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27089 | TimerSw_Tuesday_7_Heat |  | Only for AC | 0 | 100 | 0
27090 | TimeSw_Tuesday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27091 | TimeSw_Tuesday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27092 | TimeSw_Tuesday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27093 | TimeSw_Tuesday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27094 | TimerSw_Tuesday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27095 | TimerSw_Tuesday_8_Heat |  | Only for AC | 0 | 100 | 0
27096 | TimeSw_Wensday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27097 | TimeSw_Wensday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27098 | TimeSw_Wensday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27099 | TimeSw_Wensday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27100 | TimerSw_Wensday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27101 | TimerSw_Wensday_1_Heat |  | Only for AC | 0 | 100 | 0
27102 | TimeSw_Wensday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27103 | TimeSw_Wensday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27104 | TimeSw_Wensday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27105 | TimeSw_Wensday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27106 | TimerSw_Wensday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27107 | TimerSw_Wensday_2_Heat |  | Only for AC | 0 | 100 | 0
27108 | TimeSw_Wensday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27109 | TimeSw_Wensday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27110 | TimeSw_Wensday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27111 | TimeSw_Wensday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27112 | TimerSw_Wensday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27113 | TimerSw_Wensday_3_Heat |  | Only for AC | 0 | 100 | 0
27114 | TimeSw_Wensday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27115 | TimeSw_Wensday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27116 | TimeSw_Wensday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27117 | TimeSw_Wensday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27118 | TimerSw_Wensday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27119 | TimerSw_Wensday_4_Heat |  | Only for AC | 0 | 100 | 0
27120 | TimeSw_Wensday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27121 | TimeSw_Wensday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27122 | TimeSw_Wensday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27123 | TimeSw_Wensday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27124 | TimerSw_Wensday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27125 | TimerSw_Wensday_5_Heat |  | Only for AC | 0 | 100 | 0
27126 | TimeSw_Wensday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27127 | TimeSw_Wensday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27128 | TimeSw_Wensday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27129 | TimeSw_Wensday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27130 | TimerSw_Wensday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27131 | TimerSw_Wensday_6_Heat |  | Only for AC | 0 | 100 | 0
27132 | TimeSw_Wensday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27133 | TimeSw_Wensday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27134 | TimeSw_Wensday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27135 | TimeSw_Wensday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27136 | TimerSw_Wensday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27137 | TimerSw_Wensday_7_Heat |  | Only for AC | 0 | 100 | 0
27138 | TimeSw_Wensday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27139 | TimeSw_Wensday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27140 | TimeSw_Wensday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27141 | TimeSw_Wensday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27142 | TimerSw_Wensday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27143 | TimerSw_Wensday_8_Heat |  | Only for AC | 0 | 100 | 0
27144 | TimeSw_Thursday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27145 | TimeSw_Thursday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27146 | TimeSw_Thursday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27147 | TimeSw_Thursday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27148 | TimerSw_Thursday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27149 | TimerSw_Thursday_1_Heat |  | Only for AC | 0 | 100 | 0
27150 | TimeSw_Thursday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27151 | TimeSw_Thursday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27152 | TimeSw_Thursday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27153 | TimeSw_Thursday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27154 | TimerSw_Thursday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27155 | TimerSw_Thursday_2_Heat |  | Only for AC | 0 | 100 | 0
27156 | TimeSw_Thursday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27157 | TimeSw_Thursday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27158 | TimeSw_Thursday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27159 | TimeSw_Thursday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27160 | TimerSw_Thursday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27161 | TimerSw_Thursday_3_Heat |  | Only for AC | 0 | 100 | 0
27162 | TimeSw_Thursday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27163 | TimeSw_Thursday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27164 | TimeSw_Thursday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27165 | TimeSw_Thursday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27166 | TimerSw_Thursday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27167 | TimerSw_Thursday_4_Heat |  | Only for AC | 0 | 100 | 0
27168 | TimeSw_Thursday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27169 | TimeSw_Thursday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27170 | TimeSw_Thursday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27171 | TimeSw_Thursday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27172 | TimerSw_Thursday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27173 | TimerSw_Thursday_5_Heat |  | Only for AC | 0 | 100 | 0
27174 | TimeSw_Thursday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27175 | TimeSw_Thursday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27176 | TimeSw_Thursday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27177 | TimeSw_Thursday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27178 | TimerSw_Thursday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27179 | TimerSw_Thursday_6_Heat |  | Only for AC | 0 | 100 | 0
27180 | TimeSw_Thursday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27181 | TimeSw_Thursday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27182 | TimeSw_Thursday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27183 | TimeSw_Thursday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27184 | TimerSw_Thursday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27185 | TimerSw_Thursday_7_Heat |  | Only for AC | 0 | 100 | 0
27186 | TimeSw_Thursday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27187 | TimeSw_Thursday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27188 | TimeSw_Thursday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27189 | TimeSw_Thursday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27190 | TimerSw_Thursday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27191 | TimerSw_Thursday_8_Heat |  | Only for AC | 0 | 100 | 0
27192 | TimeSw_Friday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27193 | TimeSw_Friday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27194 | TimeSw_Friday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27195 | TimeSw_Friday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27196 | TimerSw_Friday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27197 | TimerSw_Friday_1_Heat |  | Only for AC | 0 | 100 | 0
27198 | TimeSw_Friday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27199 | TimeSw_Friday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27200 | TimeSw_Friday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27201 | TimeSw_Friday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27202 | TimerSw_Friday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27203 | TimerSw_Friday_2_Heat |  | Only for AC | 0 | 100 | 0
27204 | TimeSw_Friday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27205 | TimeSw_Friday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27206 | TimeSw_Friday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27207 | TimeSw_Friday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27208 | TimerSw_Friday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27209 | TimerSw_Friday_3_Heat |  | Only for AC | 0 | 100 | 0
27210 | TimeSw_Friday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27211 | TimeSw_Friday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27212 | TimeSw_Friday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27213 | TimeSw_Friday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27214 | TimerSw_Friday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27215 | TimerSw_Friday_4_Heat |  | Only for AC | 0 | 100 | 0
27216 | TimeSw_Friday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27217 | TimeSw_Friday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27218 | TimeSw_Friday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27219 | TimeSw_Friday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27220 | TimerSw_Friday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27221 | TimerSw_Friday_5_Heat |  | Only for AC | 0 | 100 | 0
27222 | TimeSw_Friday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27223 | TimeSw_Friday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27224 | TimeSw_Friday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27225 | TimeSw_Friday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27226 | TimerSw_Friday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27227 | TimerSw_Friday_6_Heat |  | Only for AC | 0 | 100 | 0
27228 | TimeSw_Friday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27229 | TimeSw_Friday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27230 | TimeSw_Friday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27231 | TimeSw_Friday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27232 | TimerSw_Friday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27233 | TimerSw_Friday_7_Heat |  | Only for AC | 0 | 100 | 0
27234 | TimeSw_Friday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27235 | TimeSw_Friday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27236 | TimeSw_Friday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27237 | TimeSw_Friday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27238 | TimerSw_Friday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27239 | TimerSw_Friday_8_Heat |  | Only for AC | 0 | 100 | 0
27240 | TimeSw_Saturday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27241 | TimeSw_Saturday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27242 | TimeSw_Saturday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27243 | TimeSw_Saturday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27244 | TimerSw_Saturday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27245 | TimerSw_Saturday_1_Heat |  | Only for AC | 0 | 100 | 0
27246 | TimeSw_Saturday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27247 | TimeSw_Saturday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27248 | TimeSw_Saturday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27249 | TimeSw_Saturday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27250 | TimerSw_Saturday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27251 | TimerSw_Saturday_2_Heat |  | Only for AC | 0 | 100 | 0
27252 | TimeSw_Saturday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27253 | TimeSw_Saturday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27254 | TimeSw_Saturday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27255 | TimeSw_Saturday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27256 | TimerSw_Saturday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27257 | TimerSw_Saturday_3_Heat |  | Only for AC | 0 | 100 | 0
27258 | TimeSw_Saturday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27259 | TimeSw_Saturday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27260 | TimeSw_Saturday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27261 | TimeSw_Saturday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27262 | TimerSw_Saturday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27263 | TimerSw_Saturday_4_Heat |  | Only for AC | 0 | 100 | 0
27264 | TimeSw_Saturday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27265 | TimeSw_Saturday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27266 | TimeSw_Saturday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27267 | TimeSw_Saturday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27268 | TimerSw_Saturday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27269 | TimerSw_Saturday_5_Heat |  | Only for AC | 0 | 100 | 0
27270 | TimeSw_Saturday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27271 | TimeSw_Saturday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27272 | TimeSw_Saturday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27273 | TimeSw_Saturday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27274 | TimerSw_Saturday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27275 | TimerSw_Saturday_6_Heat |  | Only for AC | 0 | 100 | 0
27276 | TimeSw_Saturday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27277 | TimeSw_Saturday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27278 | TimeSw_Saturday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27279 | TimeSw_Saturday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27280 | TimerSw_Saturday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27281 | TimerSw_Saturday_7_Heat |  | Only for AC | 0 | 100 | 0
27282 | TimeSw_Saturday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27283 | TimeSw_Saturday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27284 | TimeSw_Saturday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27285 | TimeSw_Saturday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27286 | TimerSw_Saturday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27287 | TimerSw_Saturday_8_Heat |  | Only for AC | 0 | 100 | 0
27288 | TimeSw_Sunday_1_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27289 | TimeSw_Sunday_1_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27290 | TimeSw_Sunday_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27291 | TimeSw_Sunday_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27292 | TimerSw_Sunday_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27293 | TimerSw_Sunday_1_Heat |  | Only for AC | 0 | 100 | 0
27294 | TimeSw_Sunday_2_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27295 | TimeSw_Sunday_2_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27296 | TimeSw_Sunday_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27297 | TimeSw_Sunday_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27298 | TimerSw_Sunday_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27299 | TimerSw_Sunday_2_Heat |  | Only for AC | 0 | 100 | 0
27300 | TimeSw_Sunday_3_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27301 | TimeSw_Sunday_3_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27302 | TimeSw_Sunday_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27303 | TimeSw_Sunday_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27304 | TimerSw_Sunday_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27305 | TimerSw_Sunday_3_Heat |  | Only for AC | 0 | 100 | 0
27306 | TimeSw_Sunday_4_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27307 | TimeSw_Sunday_4_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27308 | TimeSw_Sunday_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27309 | TimeSw_Sunday_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27310 | TimerSw_Sunday_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27311 | TimerSw_Sunday_4_Heat |  | Only for AC | 0 | 100 | 0
27312 | TimeSw_Sunday_5_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27313 | TimeSw_Sunday_5_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27314 | TimeSw_Sunday_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27315 | TimeSw_Sunday_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27316 | TimerSw_Sunday_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27317 | TimerSw_Sunday_5_Heat |  | Only for AC | 0 | 100 | 0
27318 | TimeSw_Sunday_6_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27319 | TimeSw_Sunday_6_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27320 | TimeSw_Sunday_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27321 | TimeSw_Sunday_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27322 | TimerSw_Sunday_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27323 | TimerSw_Sunday_6_Heat |  | Only for AC | 0 | 100 | 0
27324 | TimeSw_Sunday_7_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27325 | TimeSw_Sunday_7_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27326 | TimeSw_Sunday_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27327 | TimeSw_Sunday_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27328 | TimerSw_Sunday_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27329 | TimerSw_Sunday_7_Heat |  | Only for AC | 0 | 100 | 0
27330 | TimeSw_Sunday_8_OnHourMin |  |  | 0:00 | 23:59 | 24:00
27331 | TimeSw_Sunday_8_OffHourMin |  |  | 0:00 | 23:59 | 24:00
27332 | TimeSw_Sunday_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
27333 | TimeSw_Sunday_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
27334 | TimerSw_Sunday_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
27335 | TimerSw_Sunday_8_Heat |  | Only for AC | 0 | 100 | 0

## TIME_SWITCH_YEAR
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Time_switch register (Factory reset set to default)
28000 | TimeSWYear_Enable |  | Time switch 1 Year enable | 0 | 1 | 1 | DISABLE ENABLE
28001 | TimeSwY_1_OnDay |  |  | 1 | 31 | 1
28002 | TimeSwY_1_OnMonth |  |  | 1 | 12 | 1
28003 | TimeSwY_1_OffDay |  |  | 1 | 31 | 1
28004 | TimeSwY_1_OffMonth |  |  | 1 | 31 | 1
28005 | TimeSwY_1_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28006 | TimeSwY_1_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28007 | TimeSwY_1_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28008 | TimeSwY_1_Heat |  | Only for AC | 0 | 100 | 0
28009 | TimeSwY_2_OnDay |  |  | 1 | 31 | 1
28010 | TimeSwY_2_OnMonth |  |  | 1 | 12 | 1
28011 | TimeSwY_2_OffDay |  |  | 1 | 31 | 1
28012 | TimeSwY_2_OffMonth |  |  | 1 | 31 | 1
28013 | TimeSwY_2_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28014 | TimeSwY_2_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28015 | TimeSwY_2_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28016 | TimeSwY_2_Heat |  | Only for AC | 0 | 100 | 0
28017 | TimeSwY_3_OnDay |  |  | 1 | 31 | 1
28018 | TimeSwY_3_OnMonth |  |  | 1 | 12 | 1
28019 | TimeSwY_3_OffDay |  |  | 1 | 31 | 1
28020 | TimeSwY_3_OffMonth |  |  | 1 | 31 | 1
28021 | TimeSwY_3_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28022 | TimeSwY_3_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28023 | TimeSwY_3_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28024 | TimeSwY_3_Heat |  | Only for AC | 0 | 100 | 0
28025 | TimeSwY_4_OnDay |  |  | 1 | 31 | 1
28026 | TimeSwY_4_OnMonth |  |  | 1 | 12 | 1
28027 | TimeSwY_4_OffDay |  |  | 1 | 31 | 1
28028 | TimeSwY_4_OffMonth |  |  | 1 | 31 | 1
28029 | TimeSwY_4_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28030 | TimeSwY_4_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28031 | TimeSwY_4_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28032 | TimeSwY_4_Heat |  | Only for AC | 0 | 100 | 0
28033 | TimeSwY_5_OnDay |  |  | 1 | 31 | 1
28034 | TimeSwY_5_OnMonth |  |  | 1 | 12 | 1
28035 | TimeSwY_5_OffDay |  |  | 1 | 31 | 1
28036 | TimeSwY_5_OffMonth |  |  | 1 | 31 | 1
28037 | TimeSwY_5_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28038 | TimeSwY_5_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28039 | TimeSwY_5_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28040 | TimeSwY_5_Heat |  | Only for AC | 0 | 100 | 0
28041 | TimeSwY_6_OnDay |  |  | 1 | 31 | 1
28042 | TimeSwY_6_OnMonth |  |  | 1 | 12 | 1
28043 | TimeSwY_6_OffDay |  |  | 1 | 31 | 1
28044 | TimeSwY_6_OffMonth |  |  | 1 | 31 | 1
28045 | TimeSwY_6_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28046 | TimeSwY_6_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28047 | TimeSwY_6_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28048 | TimeSwY_6_Heat |  | Only for AC | 0 | 100 | 0
28049 | TimeSwY_7_OnDay |  |  | 1 | 31 | 1
28050 | TimeSwY_7_OnMonth |  |  | 1 | 12 | 1
28051 | TimeSwY_7_OffDay |  |  | 1 | 31 | 1
28052 | TimeSwY_7_OffMonth |  |  | 1 | 31 | 1
28053 | TimeSwY_7_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28054 | TimeSwY_7_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28055 | TimeSwY_7_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28056 | TimeSwY_7_Heat |  | Only for AC | 0 | 100 | 0
28057 | TimeSwY_8_OnDay |  |  | 1 | 31 | 1
28058 | TimeSwY_8_OnMonth |  |  | 1 | 12 | 1
28059 | TimeSwY_8_OffDay |  |  | 1 | 31 | 1
28060 | TimeSwY_8_OffMonth |  |  | 1 | 31 | 1
28061 | TimeSwY_8_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28062 | TimeSwY_8_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28063 | TimeSwY_8_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28064 | TimeSwY_8_Heat |  | Only for AC | 0 | 100 | 0
28065 | TimeSwY_9_OnDay |  |  | 1 | 31 | 1
28066 | TimeSwY_9_OnMonth |  |  | 1 | 12 | 1
28067 | TimeSwY_9_OffDay |  |  | 1 | 31 | 1
28068 | TimeSwY_9_OffMonth |  |  | 1 | 31 | 1
28069 | TimeSwY_9_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28070 | TimeSwY_9_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28071 | TimeSwY_9_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28072 | TimeSwY_9_Heat |  | Only for AC | 0 | 100 | 0
28073 | TimeSwY_10_OnDay |  |  | 1 | 31 | 1
28074 | TimeSwY_10_OnMonth |  |  | 1 | 12 | 1
28075 | TimeSwY_10_OffDay |  |  | 1 | 31 | 1
28076 | TimeSwY_10_OffMonth |  |  | 1 | 31 | 1
28077 | TimeSwY_10_AirFlow |  | Range set according locality (FACTORY SET: 10102 and 10110 …10119) and Ventilation mode (SERVICE_HARD: 25000): MANUAL = ‰ of fan power CAV for EU = m3/h CAV - for USA = cfm DCV, VAV, VAV C4 - not available | - | -
28078 | TimeSwY_10_Temp |  | Range according locality (FACTORY SET: 10102): EU = °C USA = F and Setpoint sensor selection (SERVICE:20001): Supply duct (15-45°C; 59-113F) Extract duct (15-30°C; 59-95F) Room (15-30°C; 59-86F) | - | -
28079 | TimeSwY_10_Mode |  | 0 - Manual 1 - Auto 2 - Pseudo OFF | 0 | 2 | 0
28080 | TimeSwY_10_Heat |  | Only for AC | 0 | 100 | 0

## ERROR_LOG_AHU
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Error_log register (Factory reset set to default)
30000 | year
30001 | month
30002 | day
30003 | hour
30004 | min
30005 | sec
30006 | bit0 |  | ON/OFF | 0 | 1 | 0
| bit1 |  | MANUAL | 0 | 1 | 1
| bit2 |  | CAV | 0 | 0 | 0
| bit3 |  | VAV | 0 | 0 | 0
| bit4 |  | DCV | 0 | 1 | 0
| bit5 |  | Fire | 0 | 1 | 0
| bit6 |  | Boost | 0 | 1 | 0
| bit7 |  | Nobody (Nonoccupied) | 0 | 1 | 0
| bit8 |  | Freecooling | 0 | 1 | 0
| bit9 |  | Timeswitch | 0 | 1 | 0
| bit10 |  | Calibration | 0 | 1 | 0
| bit11 |  | Cooldown | 0 | 1 | 0
| bit12 |  | DirectControl | 0 | 1 | 0
| bit13 |  | FilterInfo | 0 | 1 | 0
| bit14 |  | CfgFileError | 0 | 1 | 0
| bit15 |  | Overheat | 0 | 1 | 0
Unit global status2
30007 | bit0 |  | WaterHeater_antifreeze_protection | 0 | 1 | 0
| bit1 |  | WaterHeater waiting for hot water | 0 | 1 | 0
| bit2 |  | WaterHeater waiting for supply air temperature | 0 | 1 | 0
| bit3 |  | WCO searching inlet water temp (cold/hot) | 0 | 1 | 0
| bit4 |  | Recirculation | 0 | 1 | 0
| bit5 |  | Simulation | 0 | 1 | 0
| bit6 |  | Prefreecooling | 0 | 1 | 0
| bit7 |  | Temp Flow Reduction
| bit8 |  | PassiveHouseRestriction
| bit9 |  | AdbActive
Software error1
30008 | bit0 |  | SwFanInletError | 0 | 1
| bit1 |  | SwFanOutletError | 0 | 1
| bit2 |  | SwFilterInletError | 0 | 1
| bit3 |  | SwFilterOutletError | 0 | 1
| bit4 |  | SwFilterInletWarning | 0 | 1
| bit5 |  | SwFilterOutletWarning | 0 | 1
| bit6 |  | SwPreheater1Error | 0 | 1
| bit7 |  | SwPostheater1Error | 0 | 1
| bit8 |  | SwPostheater2Error | 0 | 1
| bit9 |  | SwPreheater2Error | 0 | 1
| bit10 |  | SwAQS SensorError | 0 | 1
| bit11 |  | SwRotaryWheelError | 0 | 1
| bit12 |  | SwADBError | 0 | 1
| bit13 |  | SwDXError | 0 | 1
| bit14 |  | SwDXDefrost | 0 | 1
| bit15 |  | SwCondensateDrain | 0 | 1
Software error2
30009 | bit0 |  | SwGError
| bit1 |  | SwGlobalError
| bit2 |  | SwKError
| bit3 |  | FilterInfo
| bit4 |  | CfgFileError
| bit5 |  | SwFilterHepaError
| bit6 |  | SwFilterHepaWarning
Sensor status1
30010 | bit0 |  | TempEXT1St | 0 | 1 | 0
| bit1 |  | TempEXT2St | 0 | 1 | 0
| bit2 |  | TempEXT3St | 0 | 1 | 0
| bit3 |  | TempEXT4St (module B) | 0 | 0 | 0
| bit4 |  | TempINT0St (module B) | 0 | 0 | 0
| bit5 |  | TempINT1St | 0 | 1 | 0
| bit6 |  | TempINT2St | 0 | 1 | 0
| bit7 |  | TempWInSt (module B) | 0 | 0 | 0
| bit8 |  | TempWOutSt (module B) | 0 | 0 | 0
| bit9 |  | TempRoomSt | 0 | 1 | 0
| bit10 |  | SensorFilterInSt | 0 | 0 | 0
| bit11 |  | SensorFilterOutSt | 0 | 0 | 0
| bit12 |  | SensorFanInletSt | 0 | 0 | 0
| bit13 |  | SensorFanOutSt | 0 | 0 | 0
| bit14 |  | SensorPressSt | 0 | 0 | 0
| bit15 |  | SensorFlowAlaramSt | 0 | 0 | 0
Sensor status2
30011 | bit0 |  | AqsSensorSt | 0 | 0 | 0
| bit1 |  | SensorRHRecSt | 0 | 0 | 0
| bit2 |  | OutsideTempSensorBmsSt | 0 | 0 | 0
| bit3 |  | SensorRHSt | 0 | 0 | 0
| bit4 |  | Sensor Filter Hepa
Input Status1
30012 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0 | 0
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0 | 0
| bit2 |  | Status DI_3_Ext_Control | 0 | 1 | 0
| bit3 |  | Status DI_4_Nobody (FIRE optional) | 0 | 1 | 0
| bit4 |  | Status DI_5_Boost | 0 | 1 | 0
| bit5 |  | Status_DI_TACHO_1 | 0 | 1 | 0
| bit6 |  | Status_DI_TACHO_2 (Rotary wheel error) | 0 | 1 | 0
| bit7 |  | Status_DI_TACHO_3 | 0 | 1 | 0
| bit8 |  | Status_DI_TACHO_4 | 0 | 1 | 0
| bit9 |  | Status_DI_TACHO_5 | 0 | 1 | 0
| bit10 |  | Status_DI_TACHO_6 | 0 | 1 | 0
| bit11 |  | Status_DI_TACHO_7 | 0 | 1 | 0
| bit12 |  | Status_DI_TACHO_8 | 0 | 1 | 0
| bit13 |  | Status_DI_6_ADB_DX_error (module B) | 0 | 1 | 0
| bit14 |  | Status_DI_7_HeatPumpDefrost (module B) | 0 | 1 | 0
| bit15 |  | Status_DI_8_HeatPumpError (module B) | 0 | 1 | 0
Input Status2
30013 | bit0 |  | Status_DI_9_FIRE (module B) | 0 | 1 | 0
| bit1 |  | Status_DI_10_CondensDrain (module B) | 0 | 1 | 0
Output Status1
30014 | bit0 |  | Status_DO_1_Flap_inlet | 0 | 1 | 0
| bit1 |  | Status_DO_2_Flap_outlet | 0 | 1 | 0
| bit2 |  | Status_DO_3_Run_indication | 0 | 1 | 0
| bit3 |  | Status_DO_4_Water_pump (module A) | 0 | 1 | 0
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1 | 0
| bit5 |  | Status_DO_6_Error (module B) | 0 | 1 | 0
| bit6 |  | Status_DO_7_ADB_on_off (module B) | 0 | 1 | 0
| bit7 |  | Status_DO_8_HeatPump_on_off (module B) | 0 | 1 | 0
| bit8 |  | Status_DO_9_WaterPump_on_off (module B) | 0 | 1 | 0
Hardware Status1
30015 | bit0 |  | FRAM
| bit1 |  | EEPROM | 0 | 1 | 0
| bit2 |  | Ethernet | 0 | 1 | 0
| bit3 |  | RTC_Cell | 0 | 1 | 0
| bit4 |  | MainPower | 0 | 1 | 0
| bit5 |  | ControlPanel | 0 | 1 | 0
| bit6 |  | B_module | 0 | 1 | 0
| bit7 |  | C_module_In_Press | 0 | 1 | 0
| bit8 |  | C_module_Out_Press | 0 | 1 | 0
| bit9 |  | C_module_In_Filter_Press | 0 | 1 | 0
| bit10 |  | C_module_Out_Filter_Press | 0 | 1 | 0
| bit11 |  | C_module_Duct_Press | 0 | 1 | 0
| bit12 |  | C_module_C4_Duct_Press | 0 | 1 | 0
| bit13 |  | C_module_RH | 0 | 1 | 0
| bit14 |  | AQS | 0 | 1 | 0
| bit15 |  | USB_over_current | 0 | 1 | 0
Hardware Status2
30016 | bit0 |  | Ethernet_communication | 0 | 1 | 0
| bit9 |  | C_module_Hepa_Press | 0 | 1 | 0
| bit2 |  |  | 0 | 1 | 0
| bit3 |  |  | 0 | 1 | 0
| bit4 |  |  | 0 | 1 | 0
| bit5 |  |  | 0 | 1 | 0
| bit6 |  |  | 0 | 1 | 0
| bit7 |  |  | 0 | 1 | 0
| bit8 |  |  | 0 | 1 | 0
| bit9 |  |  | 0 | 1 | 0
| bit10 |  |  | 0 | 1 | 0
| bit11 |  |  | 0 | 1 | 0
| bit12 |  |  | 0 | 1 | 0
| bit13 |  |  | 0 | 1 | 0
| bit14 |  |  | 0 | 1 | 0
| bit15 |  |  | 0 | 1 | 0
30017 | AirFlowInletFanDemand |  | m3/h (cfm) | 0 | 0xffff | 0
30018 | AirFlowOutletFanDemand |  | m3/h (cfm) | 0 | 0xffff | 0
30019 | AirFlowInletFanManual |  | ‰ of fan power | 0 | 1000 | 0
30020 | AirFlowOutletFanManual |  | ‰ of fan power | 0 | 1000 | 0
30021 | AirFlowInletFan |  | m3/h (cfm) | 0 | 0xffff | 0
30022 | AirFlowOutletFan |  | m3/h (cfm) | 0 | 0xffff | 0
30023 | TempEXT1 |  | °C (°F) | -40 (-40) | 100 (212) | 0
30024 | TempEXT2 |  | °C (°F) | -40 (-40) | 100 (212) | 3
30025 | TempEXT3 |  | °C (°F) | -40 (-40) | 100 (212) | 4
30026 | TempEXT4 |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 5
30027 | TempINT0 |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 20
30028 | TempINT1 |  | °C (°F) | -40 (-40) | 100 (212) | 20
30029 | TempINT2 |  | °C (°F) | -40 (-40) | 100 (212) | 4
30030 | TempWIn |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 22
30031 | TempWOut |  | °C (°F) (module B) | -40 (-40) | 100 (212) | 4
30032 | TempRoom |  | °C (°F) | -40 (-40) | 100 (212) | 21
30033 | SensorFilterIn |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30034 | SensorFilterOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30035 | SensorFanInlet |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30036 | SensorFanOut |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30037 | SensorPress |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30038 | SensorFlowAlarm |  |  | 0 | 0 | 0
30039 | AqsSensorValue |  | % | 0 | 100 | 0
30040 | SensorRHRec |  | % | 0 | 100 | 0
30041 | SensorRH |  | % (module C) | 0 | 100 | 0
30042 | PowerPreheater1 |  | % | 0 | 100 | 0
30043 | PowerPreheater2 |  | % (module B) | 0 | 100 | 0
30044 | PowerPostheater1 |  | % | 0 | 100 | 0
30045 | PowerPostheater2 |  | % (module B) | 0 | 100 | 0
30046 | PowerPostheater3 |  | % (module B) | 0 | 100 | 0
30047 | BypassPossition |  | % | 0 | 100 | 0
30048 | Recirculation |  | % (module B) | 0 | 100 | 0
30049 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212) | 0
30050 | InletFilterPercent |  | % | 0 | 100 | 0
30051 | OutletFilterPercent |  | % | 0 | 100 | 0
30052 | dummy |  |  | 0 | 0xFFFF | 0
30053 | SensorFilterhEPA |  | Pa (in H2O) | 0 (0) | 2000 (8,029) | 0
30054 | HepaFilterPercent |  | % | 0 | 100 | 0

## ERROR_LOG_AC
Address | Name | Structure | Info | Min. Value | Max. Value | Enum
Status regiSter - read only (Factory reset no effect)
30000 | day
30001 | month
30002 | hour
30003 | min
Unit global status
30004 | bit0 |  | OFF/ON | 0 | 1
| bit1 |  | Automatic heat | 0 | 1
| bit2 |  | Automatic flow | 0 | 1
| bit3 |  | NightReduction | 0 | 1
| bit4 |  | Timeswitch | 0 | 1
| bit5 |  | Cooldown | 0 | 1
| bit6 |  | WaterHeater_antifreeze_protection | 0 | 1
| bit7 |  | WaterHeater waiting for hot water | 0 | 1
| bit8 |  | SummerHeat | 0 | 1
| bit8 |  | OpenDoor | 0 | 1
| bit10 |  | DoorAfterRunning | 0 | 1
Software error
30005 | bit0 |  | SwFanError | 0 | 1
| bit1 |  | SwFanError1 | 0 | 1
| bit2 |  | SwFilterError | 0 | 1
| bit3 |  | SwFilterWarning | 0 | 1
| bit4 |  | SwHeaterError | 0 | 1
| bit5 |  | SwDXError | 0 | 1
| bit6 |  | SwDXDefrost | 0 | 1
| bit7 |  | SwGlobalError | 0 | 1
| bit8 |  | CfgFileError | 0 | 1
Software error 1
30006 | reserva
Sensor status
30007 | bit0 |  | TempEXT1St | 0 | 1
| bit1 |  | TempEXT3St | 0 | 1
| bit2 |  | TempINT1St | 0 | 1
| bit3 |  | TempWOutSt | 0 | 1
| bit4 |  | TempRoomSt | 0 | 1
| bit5 |  | OutsideTempSensorBmsSt | 0 | 1
| bit6 |  | RoomTempSensorBmsSt | 0 | 1
| bit7 |  | SensorFlowAlaramSt | 0 | 1
Input Status
30008 | bit0 |  | Status DI_1_SafetyTherm1 | 0 | 0
| bit1 |  | Status DI_2_SafetyTherm2 | 0 | 0
| bit2 |  | Status DI_3_Ext_Control | 0 | 1
| bit3 |  | Status DI_4_RoomThermostat | 0 | 1
| bit4 |  | Status DI_5_Door | 0 | 1
| bit5 |  | Status_DI_TACHO_1 | 0 | 1
| bit6 |  | Status_DI_TACHO_2 | 0 | 1
| bit7 |  | Status_DI_TACHO_3 | 0 | 1
| bit8 |  | Status_DI_TACHO_4 | 0 | 1
| bit9 |  | Status_DI_TACHO_5 | 0 | 1
| bit10 |  | Status_DI_TACHO_6 | 0 | 1
| bit11 |  | Status_DI_TACHO_7 | 0 | 1
| bit12 |  | Status_DI_TACHO_8 | 0 | 1
| bit13 |  | Status_DI_6_ADB_DX_error | 0 | 1
| bit14 |  | Status_DI_7_HeatPumpDefrost | 0 | 1
| bit15 |  | Status_DI_8_HeatPumpError | 0 | 1
Output Status
30009 | bit0 |  | Status_DO_1_Heat1 | 0 | 1
| bit1 |  | Status_DO_1_Heat2 | 0 | 1
| bit2 |  | Status_DO_3_Run_indication | 0 | 1
| bit3 |  | Status_DO_4_Error | 0 | 1
| bit4 |  | Status_DO_5_Heat_cool | 0 | 1
| bit5 |  | Status_DO_6_Water_pump | 0 | 1
30010 | AirFlowFanManual |  | ‰ of fan power | 0 | 1000
30011 | TempEXT1 |  | °C (°F) | -40 (-40) | 100 (212)
30012 | TempEXT3 |  | °C (°F) | -40 (-40) | 100 (212)
30013 | TempINT1 |  | °C (°F) | -40 (-40) | 100 (212)
30014 | TempWOut |  | °C (°F) | -40 (-40) | 100 (212)
30015 | TempRoom |  | °C (°F) | -40 (-40) | 100 (212)
30016 | SensorFlowAlarm |  |  | 0 | 1
30017 | PowerHeater |  | % | 0 | 100
30018 | TempOutsideBMS |  | °C (°F) | -40 (-40) | 100 (212)
30019 | RoomBMS |  | °C (°F) | -40 (-40) | 101 (212)
30020 | FilterPercent |  | % | 0 | 100
30021 | dummy |  |  | 0 | 0xFFFF
Tacho Board Status
30022 | bit1 |  | Status_DI_TACHO_1 | 0 | 1
| bit2 |  | Status_DI_TACHO_2 | 0 | 1
| bit3 |  | Status_DI_TACHO_3 | 0 | 1
| bit4 |  | Status_DI_TACHO_4 | 0 | 1
| bit5 |  | Status_DI_TACHO_5 | 0 | 1
| bit6 |  | Status_DI_TACHO_6 | 0 | 1
| bit7 |  | Status_DI_TACHO_7 | 0 | 1
| bit8 |  | Status_DI_TACHO_8 | 0 | 1
| bit9 |  | Status_DI_TACHO_9 | 0 | 1
| bit10 |  | Status_DI_TACHO_10 | 0 | 1
30023 | Reserva
30024 | Reserva

## ERROR_LOG_DRIVER
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
29900 | Buffer select |  |  | 0 | 14 | 0
29901 | Bank select |  |  | 0 | 1 | 0
29902 | clear Error log |  |  | 0 | 1 | 0

## NETWORK
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
26000 | IP adress 0.x.x.x |  | IP adress part1 (0x00-0xFF) | 0 | 255 | 192
26001 | IP adress x.0.x.x |  | IP adress part2 (0x00-0xFF) | 0 | 255 | 168
26002 | IP adress x.x.0.x |  | IP adress part3 (0x00-0xFF) | 0 | 255 | 0
26003 | IP adress x.x.x.0 |  | IP adress part4 (0x00-0xFF) | 0 | 255 | 1
26004 | Mask 0.x.x.x |  | Mask part1 (0x00-0xFF) | 0 | 255 | 255
26005 | Mask x.0.x.x |  | Mask part2 (0x00-0xFF) | 0 | 255 | 255
26006 | Mask x.x.0.x |  | Mask part3 (0x00-0xFF) | 0 | 255 | 255
26007 | Mask x.x.x.0 |  | Mask part4 (0x00-0xFF) | 0 | 255 | 0
26008 | Gateway 0.x.x.x |  | Gateway part1 (0x00-0xFF) | 0 | 255 | 192
26009 | Gateway x.0.x.x |  | Gateway part2 (0x00-0xFF) | 0 | 255 | 168
26010 | Gateway x.x.0.x |  | Gateway part3 (0x00-0xFF) | 0 | 255 | 0
26011 | Gateway x.x.x.0 |  | Gateway part4 (0x00-0xFF) | 0 | 255 | 0
26012 | DHCP |  | 0 - DHCP off 1 - DHCP on | 0 | 1 | 0
26013 | ModbusPort |  | Port number 1 - 0xFFFF | 1 | 0xFFFF | 502

## CFG_UNIT
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
CFG_UNIT (Factory reset no effect)
40000 | CFG_UNIT_PASSWORD
40001 | lenght
40002 | Version
40003 | Serial_number[0]
40004 | Serial_number[1]
40005 | Serial_number[2]
40006 | Serial_number[3]
40007 | Serial_number[4]
40008 | Serial_number[5]
40009 | Serial_number[6]
40010 | Serial_number[7]
40011 | Serial_number[8]
40012 | Serial_number[9]
40013 | Serial_number[10]
40014 | Serial_number[11]
40015 | Serial_number[12]
40016 | Serial_number[13]
40017 | Serial_number[14]
40018 | Serial_number[15]
40019 | Serial_number[16]
40020 | Serial_number[17]
40021 | Serial_number[18]
40022 | Serial_number[19]
40023 | EAN[0]
40024 | EAN[1]
40025 | EAN[2]
40026 | EAN[3]
40027 | EAN[4]
40028 | EAN[5]
40029 | EAN[6]
40030 | EAN[7]
40031 | EAN[8]
40032 | EAN[9]
40033 | EAN[10]
40034 | EAN[11]
40035 | EAN[12]
40036 | EAN[13]
40037 | EAN[14]
40038 | EAN[15]
40039 | EAN[16]
40040 | EAN[17]
40041 | EAN[18]
40042 | EAN[19]
40043 | EAN_sub[0]
40044 | EAN_sub[1]
40045 | EAN_sub[2]
40046 | EAN_sub[3]
40047 | EAN_sub[4]
40048 | EAN_sub[5]
40049 | EAN_sub[6]
40050 | EAN_sub[7]
40051 | EAN_sub[8]
40052 | EAN_sub[9]
40053 | EAN_sub[10]
40054 | EAN_sub[11]
40055 | EAN_sub[12]
40056 | EAN_sub[13]
40057 | EAN_sub[14]
40058 | EAN_sub[15]
40059 | EAN_sub[16]
40060 | EAN_sub[17]
40061 | EAN_sub[18]
40062 | EAN_sub[19]
40063 | EAN_sub[20]
40064 | EAN_sub[21]
40065 | EAN_sub[22]
40066 | EAN_sub[23]
40067 | EAN_sub[24]
40068 | EAN_sub[25]
40069 | EAN_sub[26]
40070 | EAN_sub[27]
40071 | EAN_sub[28]
40072 | EAN_sub[29]
40073 | Factory_id[0]
40074 | Factory_id[1]
40075 | Factory_id[2]
40076 | Id
40077 | Locality
40078 | Default_Language
40079 | Set_GBA
40080 | Name[0]
40081 | Name[1]
40082 | Name[2]
40083 | Name[3]
40084 | Name[4]
40085 | Name[5]
40086 | Name[6]
40087 | Name[7]
40088 | Name[8]
40089 | Name[9]
40090 | Name[10]
40091 | Name_Flow
40092 | Max_Flow
40093 | Min_Flow
40094 | Step_Flow
40095 | Max_constant_press
40096 | Default_Flow
40097 | Default_Temperature
40098 | Recup
40099 | Preheater1
40100 | Preheater2
40101 | Postheater1
40102 | Postheater2
40103 | Bypass
40104 | Recirculation_Unit
40105 | Adiabatic_Unit
40106 | Reserve_Unit_1
40107 | Reserve_Unit_2
40108 | TK1
40109 | TK2
40110 | Fan_Sensor
40111 | Filter_sensor
40112 | Constant_press_sensor
40113 | CP_sensor_site
40114 | RH_dew_point_sensor
40115 | Flow_Alarm_sensor
40116 | K1_fan_inlet
40117 | K1_fan_inlet
40118 | L1_fan_inlet
40119 | K2_fan_inlet
40120 | K2_fan_inlet
40121 | L2_fan_inlet
40122 | K3_fan_inlet
40123 | K3_fan_inlet
40124 | K1_fan_outlet
40125 | K1_fan_outlet
40126 | L1_fan_outlet
40127 | K2_fan_outlet
40128 | K2_fan_outlet
40129 | L2_fan_outlet
40130 | K3_fan_outlet
40131 | K3_fan_outlet
40132 | K1_bypass
40133 | K1_bypass
40134 | K2_bypass
40135 | K2_bypass
40136 | kpfi0
40137 | kpfi0
40138 | kpfi1
40139 | kpfi1
40140 | kpfi2
40141 | kpfi2
40142 | kpfo0
40143 | kpfo0
40144 | kpfo1
40145 | kpfo1
40146 | kpfo2
40147 | kpfo2
40148 | Motor_type
40149 | Motor_PID_P
40150 | Motor_PID_I
40151 | Passive_House
40152 | Off_mode_min_flow
40153 | WhisperAir_limit
40154 | HEPA_filter
40155 | PreferManualOutput
40156 | NumOfDigitalHeaters
40157 | ARC_Timer_service
40158 | NumOfMotors
40159 | reserva
40160 | reserva
40161 | reserva
40162 | reserva

## NORDIC_SERVICE
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Nordic service register (Factory reset set to default)
43000 | Valve excercising enable |  |  | 0 | 1 | 0
43001 | Valve excercising time |  |  | 1 | 120 | 60
43002 | Valve bleeding |  |  | 0 | 30 | 0
43003 | Door close fan off enable |  |  | 0 | 1 | 0
43004 | Door close fan off temperature |  |  | 5 | 30 | 20
43005 | Door close fan off delay |  |  | 0 | 120
43006 | reserva |  |  | 0 | 0 | 0
43007 | Door fan limits open min |  |  | 15 | 40 | 20
43008 | Door fan limits open max |  |  | 40 | 100 | 100
43009 | Door fan limits close min |  |  | 15 | 40 | 20
43010 | Door fan limits close max |  |  | 40 | 100 | 100
43011 | Antifreze sensor enable |  |  | 0 | 3 | 3
| bit0 |  | Air | 0 | 1 | 1
| bit1 |  | Water | 0 | 1 | 1
43012 | Water return limit enable |  |  | 0 | 1 | 0
43013 | Water return limit temperature |  |  | 15 | 85 | 50
43014 | Outlet temp limit |  |  | 5 | 30 | 17
43015 | Alarm temp room enable |  |  | 0 | 1 | 0
43016 | Fan off temp room enable |  |  | 0 | 1 | 0
43017 | Fan off temp room |  |  | 1 | 5 | 2
43018 | Damper open |  |  | 0 | 100 | 10
43019 | Damper delay |  |  | 0 | 120 | 30
43020 | Savana fan limits min |  |  | 15 | 40 | 15
43021 | Savana fan limits max |  |  | 40 | 100 | 60
43022 | Outlet limitation room |  |  | 0 | 1
43023 | reserva |  |  | 0 | 0 | 0
43024 | reserva |  |  | 0 | 0 | 0
43025 | reserva |  |  | 0 | 0 | 0

## WIFI_SETTINGS (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Wifi Settings
13000 | State
13001 | Mode
13002 | Mode_1
13003 | NumOfSSID
13004 | NumOfSSID1
13005 | ActiveSSID
13006 | ActiveSSID1
13007 | reserva
13008 | reserva
13009 | reserva
13009 - 13041 | SSID_req
13042 - 13074 | SSID_set
13075 - 13139 | Password_set

## IBUS GateWay Status (hidden)
Address | Name | Structure | Min. Value | Max. Value | Max. Value | Default | Enum
IBUS GateWay Sensors Status
12000 | Gateway_Sensor1_s |  | 0 | 1
| Gateway_Sensor2_s |  | 0 | 1
| Gateway_Sensor3_s |  | 0 | 1
| Gateway_Sensor4_s |  | 0 | 1
| Gateway_Sensor5_s |  | 0 | 1
| Gateway_Sensor6_s |  | 0 | 1
| Gateway_Sensor7_s |  | 0 | 1
| Gateway_Sensor8_s |  | 0 | 1
| Gateway_Sensor9_s |  | 0 | 1
| Gateway_Sensor10_s |  | 0 | 1
| Gateway_Sensor11_s |  | 0 | 1
| Gateway_Sensor12_s |  | 0 | 1
| Gateway_Sensor13_s |  | 0 | 1
| Gateway_Sensor14_s |  | 0 | 1
| Gateway_Sensor15_s |  | 0 | 1
| Gateway_Sensor16_s |  | 0 | 1
12001 | Gateway_Sensor17_s |  | 0 | 1
| Gateway_Sensor18_s |  | 0 | 1
| Gateway_Sensor19_s |  | 0 | 1
| Gateway_Sensor20_s |  | 0 | 1
| Gateway_Sensor21_s |  | 0 | 1
| Gateway_Sensor22_s |  | 0 | 1
| Gateway_Sensor23_s |  | 0 | 1
| Gateway_Sensor24_s |  | 0 | 1
12002 | Sensor1 value |  | 0 | FFFF
12003 | Sensor2 value |  | 0 | FFFF
12004 | Sensor3 value |  | 0 | FFFF
12005 | Sensor4 value |  | 0 | FFFF
12006 | Sensor5 value |  | 0 | FFFF
12007 | Sensor6 value |  | 0 | FFFF
12008 | Sensor7 value |  | 0 | FFFF
12009 | Sensor8 value |  | 0 | FFFF
12010 | Sensor9 value |  | 0 | FFFF
12011 | Sensor10 value |  | 0 | FFFF
12012 | Sensor11 value |  | 0 | FFFF
12013 | Sensor12 value |  | 0 | FFFF
12014 | Sensor13 value |  | 0 | FFFF
12015 | Sensor14 value |  | 0 | FFFF
12016 | Sensor15 value |  | 0 | FFFF
12017 | Sensor16 value |  | 0 | FFFF
12018 | Sensor17 value |  | 0 | FFFF
12019 | Sensor18 value |  | 0 | FFFF
12020 | Sensor19 value |  | 0 | FFFF
12021 | Sensor20 value |  | 0 | FFFF
12022 | Sensor21 value |  | 0 | FFFF
12023 | Sensor22 value |  | 0 | FFFF
12024 | Sensor23 value |  | 0 | FFFF
12025 | Sensor24 value |  | 0 | FFFF

## BMS_TEMP_SENSORS
Address | Name | Info
23000 | RoomBms | write temperature *10
23001 | RoomBms-Status | status of sensor
23002 | OutsideBms | write temperature *10
23003 | OutsideBms-Status | status of sensor

## DIRECT_CONTROL
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
35000 | bit0 |  | Dir_Ctrl_DO_1_Flap_inlet | 0 | 1 | 0 | FLAP_CLOSED FLAP_OPEN
| bit1 |  | Dir_Ctrl_DO_2_Flap_outlet | 0 | 1 | 0 | FLAP_CLOSED FLAP_OPEN
| bit2 |  | Dir_Ctrl_DO_3_Run_indication | 0 | 1 | 0 | RUN_INDICATION NO_RUN
| bit3 |  | Dir_Ctrl_DO_4_Water_pump (module A) | 0 | 1 | 0 | W_PUMP_A_ON W_PUMP_A_OFF
| bit4 |  | Dir_Ctrl_DO_5_Heat_cool | 0 | 1 | 0 | EXCHANGER_COOL EXCHANGER_HEAT
| bit5 |  | Dir_Ctrl_DO_6_Error (module B) | 0 | 1 | 0 | ERROR_B_OK ERROR_B_ERROR
| bit6 |  | Dir_Ctrl_DO_7_ADB_on_off (module B) | 0 | 1 | 0 | ADB_ON ADB_OFF
| bit7 |  | Dir_Ctrl_DO_8_HeatPump_on_off (module B) | 0 | 1 | 0 | HEAT_PUMP_ON HEAT_PUMP_OFF
| bit8 |  | Dir_Ctrl_DO_9_WaterPump_on_off (module B) | 0 | 1 | 0 | W_PUMP_B_ON W_PUMP_B_OFF
35001 | AirFlowInletFanManual |  | Dir_Ctrl_InletFanMan (‰ of fan power) | 0 | 1000 | 0
35002 | AirFlowOutletFanManual |  | Dir_Ctrl_OutletFanMan (‰ of fan power) | 0 | 1000 | 0
35003 | PowerPreheater1 |  | % | 0 | 100 | 0
35004 | PowerPreheater2 |  | % (module B) | 0 | 100 | 0
35005 | PowerPostheater1 |  | % | 0 | 100 | 0
35006 | PowerPostheater2 |  | % (module B) | 0 | 100 | 0
35007 | PowerPostheater3 |  | % (module B) | 0 | 100 | 0
35008 | Recirculation |  | % (module B) | 0 | 100 | 0
35009 | Bypass/Rotary wheel exchanger |  | % | 0 | 100 | 0

## SIMULATION (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
36000

## FILTER_CALIBRATION (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
37000

## EEFICIENCY AND SAVINGS (hidden)
Address | Name | Structure | Info | Min. Value | Max. Value | Default | Enum
Network register (Factory reset no effect)
| AvarageRecEfficiency |  | % | 0 | 100
| AvarageAirflow |  | % | 0 | 100