FLÄKTKONVEKTORER

Takmontage

Fabrikat: EVECO AB, 031-84 08 50

Typ: SKECM52				5st

LxDxH, 819x819x329mm
RSK: 6707829

Luftmängd/ljudtryck:

Hastighet 1: 710m³/h, 25dB(A)

Hastighet 2: 1130m³/h, 38dB(A)

Hastighet 3: 1770m³/h, 48dB(A)

Motoreffekt/ström/spänning:

Max. hastighet: 108W, 230V/1

Tillbehör

Frontpanel	HTA800			5st

RSK 6707874

Integrerat luftfilter, tvättbart

Reglering

Samtliga takkassetter kompletteras med styrenhet UPAU RSK 6707870 och ventilsats (Ställdon och konstantflödesventil) FVI15.2, RSK 6704697

En gemensam manöverenhet TMB, RSK 6707886 placeras i rummet.

FAN COILS

Ceiling mounting

Manufacturer: EVECO AB, 031-84 08 50

Type: SKECM52 			5pcs

LxDxH, 819x819x329mm

RSK: 6707829

Air volume / sound pressure:

Speed 1: 710m³ / h, 25dB (A)

Speed 2: 1130m³ / h, 38dB (A)

Speed 3: 1770m³ / h, 48dB (A)

Motor power / current / voltage:

Max. speed: 108W, 230V / 1

Accessories

Front panel HTA800 			5pcs

RSK 6707874

Integrated air filter, washable

Controls

Each fan coil should be supplemented with control unit UPAU, RSK 6707870, and valve set (Actuator and constant flow valve) FVI15.2, RSK 6704697

One common control unit TMB, RSK 6707886 should be placed in the room.