## INTRODUCTION
Modbus description is valid for Modbus RTU communication
Modbus communication description is valid for all product types
Before controlling the product over the Modbus, it is necessary to read manual for the product to know exact supported functionalities of product in all modes!!!
Usage of specific registers depend on hardware product configuration (water heated, electrically heated,...) and as well also on actual used mode and settings in service menu
Each list in the document contain the same type of registers wich are used for the same purpose (example bellow)
Example 1: SHARE = holding registers (READ/WRITE) - used for control the product
Example 2: STATUS = input registers (READ only registers) - used to read out actual status of the product
Description of registers purpose in each list :
HOLDING REGISTERS - READ/WRITE | Purpose:
SERVICE | To set and check parameters in service menu of the product. Factory reset function, resets the parameters to default values
SHARE | Used for product control. Registers represent actual control commands and allows sending the control requests to the product. Registers also represent the commands from control panel or other control equipment (Android app, Service SW,...)
BMS_TEMP_SENSORs | Used for receving external sensors value from BMS
INPUT REGISTERS - READ ONLY
FACTORY | Used for manufacturer purpose
INFO | To read out informations about the product (same as info screen from control panel)
STATUS | To read out actul status of the air curtain (actual mode, air flows, temperatures, HW status, Errors,…)
SLAVE_STATUS | To read out actul status of the SLAVE air curtains (actual mode, fan speed, temperatures, HW status, Errors,…)

## FUNCTIONS
HOLDING REGISTERS | FUNC_CODE
SERVICE | 0x03,0x06,0x10
SHARE | 0x03,0x06,0x10
INPUT REGISTERS
FACTORY | 0x04
STATUS_AC | 0x04
SLAVE_AC_STATUS | 0x04
Default Modbus RTU settings
Modbus Unit Address | 1
Baudrate | 9600
Parity | ODD
Stop Bits | 1
PLC Addresses - BASE1
Values are represent as unsigned 2xByte

## INPUT-FACTORY
Address | Name | Info | Min. Value | Max. Value | Default | Enum
Factory register - read only (Factory reset no effect)
31000 | Reserved | Reserved | 0 | 65535 | 0
31001 | ID | ID unit | 0 | 65535 | 525 | Prime ID = 525
31002 | Locality | Locality of instalation | 0 | 1 | 0 | EU = 0 USA = 1
31003 | Fan_type | Type of fan | 0 | 3 | 0 | MOTOR EC = 0 MOTOR AC = 1 (reserved) MOTOR AC3 = 2 (3 stp level) MOTOR AC5 = 3 (5 stp level)
31004 | Heat_type | Type of fan heating exchanger |  |  |  | POST_HEAT_NONE = 0 ELECTRIC = 1 WATER = 2 WCO = 3 (reserved) DX = 4 (reserved) WC = 5 (reserved)
31005 | Modbus_Baudrate | Modbus Baudrate | 4800 |  | 19200 | 4800 9600 14400 19200 38400
31006 | Modbus_Parity | Modbus Parity | 0 | 2 | 1 | NONE = 0 ODD = 1 EVEN = 2
31007 | Modbus_adress_port | Modbus adress port | 1 | 247 | 1
31008 | Serial numberH | Serial number | 0 | 65535 | 0
31009 | Serial numberL | Serial number | 0 | 65535 | 0
31010 | FW_F0 | Microcontroller firmware number | 0 | 65535 | 0
31011 | FW_WT | WiFi firmware number | 0 | 65535 | 0
31012 | Motor_max_pwm_limit | Motor power limitation percent | 20 | 100 | 100
31013 | Reserved | Reserved | 0 | 65535 | 0
31014 | Reserved | Reserved | 0 | 65535 | 0
31015 | Reserved | Reserved | 0 | 65535 | 0
31016 | Reserved | Reserved | 0 | 65535 | 0
31017 | Reserved | Reserved | 0 | 65535 | 0
31018 | Reserved | Reserved | 0 | 65535 | 0
31019 | Reserved | Reserved | 0 | 65535 | 0
31020 | Reserved | Reserved | 0 | 65535 | 0
31021 | Reserved | Reserved | 0 | 65535 | 0
31022 | Reserved | Reserved | 0 | 65535 | 0

## HOLDING-SERVICE
Address | Name | Info | Min. Value | Max. Value | Default | Enum
Service register (Factory reset set to default)
40200 | Subunits | Number of subunits (modbus slaves) | 1 | 10 | 1
40201 | Cp_pin | Control panel PIN | 0 | 99 | 0 | 0 = without PIN
40202 | AutoSpeedControlEnable | Fan autospeed control - enabling function | 0 | 1 | 0
40203 | Heat_mode | Automatic heating mode enable (PID control) | 0 | 1 | 1 | 0 = disable
40204 | DoorContactFixedOverRunEnable | Door contact mode - enabling and specifying the function | 0 | 2 | 1 | Overrun mode 0 = disable 1 = time interval 2 = driving by temperature
40205 | DoorContactFixedOverRunMinflowTime | Overrun time on minimal fan speed | 5 | 300 |  | sec
40206 | DoorContactFixedOverRunMaxflowTime | Overrun time on maximal fan speed | 5 | 300 |  | sec
40207 | DoorContactFixedOverRunTempSetpoint | Setpoint for Door contact overrun function driving by temperature | 15°C / 59°F | 30°C / 86°F | 20°C / 68°F
40208 | OutsideTempSensorAirCurtain | Outside temperature sensor location | 0 | 2 | 1 | 0 = disable 1 = EXT1 temperature from modbus slave (subunit) 1 2 = BMS
40209 | DoorContactFixedOverRunTempSelect | Selection for Door OverRun sensor | 0 | 1 | 0 | 0 = CT room 1 = thermostat
40210 | TempSensorSelection | Feedback for automatic temperature control | 0 | 4 | 2 | 2 = room 3 = thermostat 4 = room BMS
40211 | PreferManualOutput |  | 0 | 1 |  | 0 = digital 1 = analog
40212 | Pid_P | PID proportional range °C/°F according Locality (adr. 31002) | 5°C / 41°F | 60°C / 140°F | 20°C / 68°F
40213 | Pid_I | PID integration time (s) | 1 | 255 | 60
40214 | Pid_D | PID derivate time (s) | 0 | 10 | 0
40215 | DoorContactLogic | Logic of door contact | 0 | 1 | 1 | 0 = NO_O 1 = NO_C
40216 | ExtCtrlLogic | Logic of external control contact | 0 | 1 | 0 | 0 = NO_O 1 = NO_C
40217 | RoomThermLogic | Logic of room thermostat contact | 0 | 1 | 0 | 0 = NO_O 1 = NO_C
40218 | ExtCtrlFunction | Function of external control contact | 0 | 1 | 0 | 0 = EXT CTRL DISABLE 1 = EXT CTRL ENABLE
40219 | AntifreezeTempAirSet | Antifreeze air temperature | 5°C / 41°F | 15°C / 59°F | 5°C / 41°F
40220 | AntifreezeTempWoutSet | Antifreeze water return temperature | 10°C / 50°F | 20°C / 68°F | 10°C / 50°F
40221 | Door_SW_local | Type of door switch (local / global) | 0 | 1 | 0 | 0 = GLOBAL DOOR SWITCH 1 = LOCAL DOOR SWITCH
40222 | Fan_tacho_enable | Enable tacho input for EC fan | 0 | 1 | 1 | 0 = DISABLE TACHO 1 = ENABLE TACHO
40223 | Alarm_heater_enable | Enable TK input for heater | 0 | 1 | 1 | 0 = TK DISABLE 1 = TK ENABLE
40224 | DoorContactEnable | Enable / disable door contact | 0 | 1 | 1 | 0 = DOOR CONTACT DISABLE 1 = DOOR CONTACT ENABLE
40225 | Filter_timer_max | Maximum time for maintenance in hours | 0 | 4500 | 4500 | 0 = DISABLE MAINTENANCE INTERVAL
40226 | AutoSpeedControlDeltaT | Delta T for automatic speed control changes | 1 | 5 | 1
40227 | SummerHeatEnable | Enable summer heat blocation | 0 | 1 | 0
40228 | Reserved | Reserved | 0 | 65535 | 0
40229 | WinterMounthStart | Mounth when winter starts | 1 | 12 | 1
40230 | WinterMounthStop | Mounth when winter ends | 1 | 12 | 1
40231 | SummerTempHeaterEnable | Limit temperature to enable heat in summer | 10°C / 50°F | 20°C / 68°F | 15°C / 59°F
40232 | Reserved | Reserved | 0 | 65535 | 0
40233 | Reserved | Reserved | 0 | 65535 | 0
40234 | Valve_excercising - enable | Enable valve excercising for water exchanger | 0 | 1 | 0 | 0 = disable
40235 | Valve_excercising - time | Time of valve excercising for water exchanger | 1 | 120 | 60
40236 | Valve_bleeding | Valve bleeding, prevence of freezing water exchanger | 0 | 30 | 0
40237 | Door_close_fan_on_off - enable | If the door is closed, it turns off the fan when enable | 0 | 1 | 0
40238 | Reserved | Reserved | 0 | 65535 | 0
40239 | Door_close_fan_on_off - delay | Time delay before fan turn off after setpoint reached | 0 | 120 | 20
40240 | Reserved | Reserved | 0 | 65535 | 0
40241 | Door_fan_limit_open_min | Minimal fan speed for open doors | EC fan 15 AC3 fan 33 AC5 fan 20 | EC fan 40 AC3 fan 66 AC5 fan 40 | EC fan 15 AC3 fan 33 AC5 fan 20
40242 | Door_fan_limit_open_max | Maximal fan speed for open doors | EC fan 40 AC3 fan 66 AC5 fan 40 | 100 | EC fan 15 AC3 fan 33 AC5 fan 20
40243 | Door_fan_limit_close_min | Minimal fan speed for close doors | EC fan 15 AC3 fan 33 AC5 fan 20 | EC fan 40 AC3 fan 66 AC5 fan 40 | EC fan 15 AC3 fan 33 AC5 fan 20
40244 | Door_fan_limit_close_max | Maximal fan speed for close doors | EC fan 40 AC3 fan 66 AC5 fan 40 | 100 | EC fan 15 AC3 fan 33 AC5 fan 20
40245 | Antifreeze_sensors_enable | bit 0 - Air | 0 | 1 | 1
|  | bit 1 - Water | 0 | 1 | 1
|  | bit 2 - TK | 0 | 1 | 0
40246 | Water_return_limit_enable | Enable water return limitation | 0 | 1 | 0
40247 | Water_return_limit - temperature | Temperature limit of return water | 15 | 85 | 50
40248 | Reserved | Reserved | 0 | 65535 | 0
40249 | Reserved | Reserved | 0 | 65535 | 0
40250 | GlobalDoorContact - enable | Enable of global door contact (from modbus subunits number 1) | 0 | 1 | 1
40251 | Reserved | Reserved | 0 | 65535 | 0
40252 | Reserved | Reserved | 0 | 65535 | 0
40253 | Reserved | Reserved | 0 | 65535 | 0
40254 | Reserved | Reserved | 0 | 65535 | 0
40255 | Reserved | Reserved | 0 | 65535 | 0
40256 | Reserved | Reserved | 0 | 65535 | 0

## INPUT-STATUS
Address | Name | Info | Min. Value | Max. Value | Enum
31100 | FW_number
Unit global status
31101 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Automatic heat | 0 | 1 | AUTOHEAT_NON AUTOHEAT_MODE
| bit2 | Automatic flow | 0 | 1 | AUTOFLOW_NON AUTOFLOW_MODE
| bit3 | Reserved | 0 | 1
| bit4 | Timeswitch | 0 | 1 | TIME_SW_NON TIME_SW_MODE
| bit5 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit6 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit7 | WaterHeater waiting for hot water | 0 | 1 | HOT_WATER_NON HOT_WATER
| bit8 | SummerHeat | 0 | 1 | WINTER SUMMER
| bit9 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit10 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit11 | Heater Under Power | 0 | 1
| bit12 | Reserved | 0 | 1
| bit13 | Reserved | 0 | 1
| bit14 | Reserved | 0 | 1
| bit15 | Reserved | 0 | 1
Software error
31102 | bit0 | SwFanError | 0 | 1
| bit1 | Reserved | 0 | 1
| bit2 | SwFilterError | 0 | 1
| bit3 | SwFilterWarning | 0 | 1
| bit4 | SwHeaterError | 0 | 1
| bit5 | Reserved | 0 | 1
| bit6 | Reserved | 0 | 1
| bit7 | SwGlobalError | 0 | 1
| bit8 | CfgFileError | 0 | 1
| bit9 | Reserved | 0 | 1
| bit10 | Alarm temp room | 0 | 1
| bit11 | AtFreeze_cnt_overflow | 0 | 1
Software error 1
31103 | Reserved
Sensor status
31104 | bit0 | TempRoomSt - Room temp. From Control Panel | 0 | 1 | OK ERROR
| bit1 | TempRoomSharedSt | 0 | 1 | OK ERROR
| bit2 | OutsideTempSensorShared | 0 | 1 | OK ERROR
| bit3 | OutsideTempSensorBmsSt | 0 | 1 | OK ERROR
| bit4 | RoomTempSensorBmsSt | 0 | 1 | OK ERROR
| bit5 | Reserved | 0 | 1 | OK ERROR
| bit6 | Reserved | 0 | 1 | OK ERROR
| bit7 | Reserved | 0 | 1 | OK ERROR
Reserved
31105 | bit0 | Status_DI_1_Door_shared | 0 | 0 | OK ERROR
| bit1 | Status_DI_2_RoomThermostat_shared | 0 | 0 | OK ERROR
| bit2 | Status_DI_3_Ext_Control_shared | 0 | 1 | OK ERROR
| bit3 | Status_DI_4_RoomThermostat_shared | 0 | 1 | OK ERROR
| bit4 | Reserved | 0 | 1 | OK ERROR
| bit5 | Reserved | 0 | 1 | OK ERROR
| bit6 | Reserved | 0 | 1 | OK ERROR
| bit7 | Reserved | 0 | 1 | OK ERROR
| bit8 | Reserved | 0 | 1 | OK ERROR
| bit9 | Reserved | 0 | 1 | OK ERROR
| bit10 | Reserved | 0 | 1 | OK ERROR
| bit11 | Reserved | 0 | 1 | OK ERROR
| bit12 | Reserved | 0 | 1 | OK ERROR
| bit13 | Reserved | 0 | 1 | OK ERROR
| bit14 | Reserved | 0 | 1 | OK ERROR
| bit15 | Reserved | 0 | 1 | OK ERROR
Output Status
31106 | bit0 | Status_DO_3_Run_indication | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit1 | Status_DO_4_Error | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit2 | Reserved | 0 | 1
| bit3 | Reserved | 0 | 1
| bit4 | Reserved | 0 | 1
| bit5 | Reserved | 0 | 1
| bit6 | Reserved | 0 | 1
| bit7 | Reserved | 0 | 1
| bit8 | Reserved | 0 | 1
| bit9 | Reserved | 0 | 1
| bit10 | Reserved | 0 | 1
| bit11 | Reserved | 0 | 1
| bit12 | Reserved | 0 | 1
| bit13 | Reserved | 0 | 1
| bit14 | Reserved | 0 | 1
| bit15 | Reserved | 0 | 1
31107 | FanSpeed | % of fan power | 0 | 100
31108 | Sensors Troom temperature | °C (°F) | -40 (-40) | 100 (212)
31109 | Sensors Troom status | °C (°F) | -40 (-40) | 100 (212)
31110 | Sensors Outside temperature | °C (°F) | -40 (-40) | 100 (212)
31111 | Sensors Outside status | °C (°F) | -40 (-40) | 100 (212)
31112 | Reserved | Reserved | 0 | 65535
31113 | PowerHeater | % | 0 | 100
31114 | TempOutsideBMS | °C (°F) | -40 (-40) | 100 (212)
31115 | RoomBMS | °C (°F) | -40 (-40) | 100 (212)
31116 | MaintanancePercent | % | 0 | 100
31117 | Reserved | Reserved | 0 | 65535
31118 | Reserved | Reserved | 0 | 65535
31119 | Temperature setpoint | °C (°F) | 5(41) | 45(113)
31120 | Reserved | Reserved | 0 | 65535
31121 | Reserved | Reserved | 0 | 65535
31122 | Reserved | Reserved | 0 | 65535
31123 | Reserved | Reserved | 0 | 65535
31124 | Reserved | Reserved | 0 | 65535
31125 | Reserved | Reserved | 0 | 65535
31126 | Reserved | Reserved | 0 | 65535
31127 | Reserved | Reserved | 0 | 65535
31128 | Reserved | Reserved | 0 | 65535
31129 | Reserved | Reserved | 0 | 65535
31130 | Reserved | Reserved | 0 | 65535
31131 | Reserved | Reserved | 0 | 65535
31132 | Reserved | Reserved | 0 | 65535
31133 | Reserved | Reserved | 0 | 65535
31134 | Reserved | Reserved | 0 | 65535

## INPUT-SLAVE_STATUS
Address | Name | Info | Min. Value | Max. Value | Enum
Slave 1
Unit global status
31200 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31201 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31202 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31203 | reserved | reserved | 0 | 0
31204 | reserved | reserved | 0 | 0
31205 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31206 | SensorFlowAlarm |  | 0 | 1
31207 | PowerHeater | % | 0 | 100
Tacho Board
31208 | reserved | reserved
31209 | reserved | reserved
Slave 2
Unit global status
31210 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31211 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31212 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31213 | reserved | reserved | 0 | 0
31214 | reserved | reserved | 0 | 0
31215 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31216 | SensorFlowAlarm |  | 0 | 1
31217 | PowerHeater | % | 0 | 100
Tacho Board
31218 | reserved | reserved
31219 | reserved | reserved
Slave 3
Unit global status
31220 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31221 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31222 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31223 | reserved | reserved | 0 | 0
31224 | reserved | reserved | 0 | 0
31225 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31226 | SensorFlowAlarm |  | 0 | 1
31227 | PowerHeater | % | 0 | 100
Tacho Board
31228 | reserved | reserved
31229 | reserved | reserved
Slave 4
Unit global status
31230 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31231 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31232 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31233 | reserved | reserved | 0 | 0
31234 | reserved | reserved | 0 | 0
31235 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31236 | SensorFlowAlarm |  | 0 | 1
31237 | PowerHeater | % | 0 | 100
Tacho Board
31238 | reserved | reserved
31239 | reserved | reserved
Slave 5
Unit global status
31240 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31241 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31242 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31243 | reserved | reserved | 0 | 0
31244 | reserved | reserved | 0 | 0
31245 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31246 | SensorFlowAlarm |  | 0 | 1
31247 | PowerHeater | % | 0 | 100
Tacho Board
31248 | reserved | reserved
31249 | reserved | reserved
Slave 6
Unit global status
31250 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31251 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31252 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31253 | reserved | reserved | 0 | 0
31254 | reserved | reserved | 0 | 0
31255 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31256 | SensorFlowAlarm |  | 0 | 1
31257 | PowerHeater | % | 0 | 100
Tacho Board
31258 | reserved | reserved
31259 | reserved | reserved
Slave 7
Unit global status
31260 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31261 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31262 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31263 | reserved | reserved | 0 | 0
31264 | reserved | reserved | 0 | 0
31265 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31266 | SensorFlowAlarm |  | 0 | 1
31267 | PowerHeater | % | 0 | 100
Tacho Board
31268 | reserved | reserved
31269 | reserved | reserved
Slave 8
Unit global status
31270 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31271 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31272 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31273 | reserved | reserved | 0 | 0
31274 | reserved | reserved | 0 | 0
31275 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31276 | SensorFlowAlarm |  | 0 | 1
31277 | PowerHeater | % | 0 | 100
Tacho Board
31278 | reserved | reserved
31279 | reserved | reserved
Slave 9
Unit global status
31280 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31281 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31282 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31283 | reserved | reserved | 0 | 0
31284 | reserved | reserved | 0 | 0
31285 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31286 | SensorFlowAlarm |  | 0 | 1
31287 | PowerHeater | % | 0 | 100
Tacho Board
31288 | reserved | reserved
31289 | reserved | reserved
Slave 10
Unit global status
31290 | bit0 | OFF/ON | 0 | 1 | OFF ON
| bit1 | Cooldown | 0 | 1 | COOLDWN_NON COOLDWN_MODE
| bit2 | WaterHeater_antifreeze_protection | 0 | 1 | AT_FREEZE_OK AT_FREEZE
| bit3 | Heater Overheat | 0 | 1
| bit4 | OpenDoor | 0 | 1 | CLOSED_DOOR OPEN_DOOR
| bit5 | DoorAfterRunning | 0 | 1 | AFTERRUNING_NON AFTERRUNING_MODE
| bit6 | SensorFlowAlaramSt | 0 | 1 | OK ERROR
| bit7 | reserved | 0 | 1
| bit8 | reserved | 0 | 1
| bit9 | TempWOutSt | 0 | 1 | OK ERROR
| bit10 | SwFanError | 0 | 1
| bit11 | SwHeaterError | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | reserved | 0 | 1
| bit14 | SwGlobalError | 0 | 1
| bit15 | Communication Error | 0 | 1
IO Status
31291 | bit0 | Status DI_1_SafetyTherm1 | 0 | 1 | OK ERROR
| bit1 | Status DI_2_Ext_Control | 0 | 1 | OK ERROR
| bit2 | Status DI_3_RoomThermostat | 0 | 1 | OK ERROR
| bit3 | Status DI_4_Door | 0 | 1 | OK ERROR
| bit4 | Status_DI_TACHO_1 | 0 | 1 | OK ERROR
| bit5 | reserved | 0 | 1
| bit6 | reserved | 0 | 1
| bit7 | reserved | 0 | 1
| bit8 | Status_DO_1_Heat1 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit9 | Status_DO_2_Heat2 | 0 | 1 | HEAT_CLOSED HEAT_OPEN
| bit10 | Status_DO_3_Water_pump | 0 | 1 | W_PUMP_A_OFF W_PUMP_A_ON
| bit11 | HeaterUnderPower | 0 | 1
| bit12 | reserved | 0 | 1
| bit13 | AtFreeze_cnt_overflow | 0 | 1
31292 | AirFlowFanManual | ‰ of fan power | 0 | 1000 | ‰ of fan power
31293 | reserved | reserved | 0 | 0
31294 | reserved | reserved | 0 | 0
31295 | TempWOut - Water return | °C (°F) | -40 (-40) | 100 (212)
31296 | SensorFlowAlarm |  | 0 | 1
31297 | PowerHeater | % | 0 | 100
Tacho Board
31298 | reserved | reserved
31299 | reserved | reserved

## HOLDING-SHARE
Address | Name | Info | Min. Value | Max. Value | Default | Enum
Share register (Factory reset set to default)
40300 | On_off |  | 0 | 1 | 1
40301 | Temper_closed_door | Temperature setpoint for closed door state | 5°C / 41°F | 45°C / 113°F | 21°C / 70°F
40302 | Heat_power_closed_door | Heating power in percent for closed door | 0 | 100 | 0
40303 | Fan_speed_closed_door | Fan speed in promile for closed door | 0 | 1000 | EC fan 150 AC3 fan 330 AC5 fan 200
40304 | Temper_open_door | Temperature setpoint for open door state | 5°C / 41°F | 45°C / 113°F | 25°C / 77°F
40305 | Heat_power_open_door | Heating power in percent for open door | 0 | 100 | 0
40306 | Fan_speed_open_door | Fan speed in promile for open door | 0 | 1000 | EC fan 150 AC3 fan 330 AC5 fan 200
40307 | Error_reset | Reset all errors | 0 | 1 | 0
40308 | Temp_sensor_reset | Reset room temperature sensor location to default | 0 | 1 | 0
40309 | Filter_timer_reset | Reset maintenance signalization | 0 | 1 | 0
40310 | Read_cfg_req | Reserved | 0 | 1 | 0
40311 | TimeSwGlobalEnable | Schedule enable | 0 | 1 | 0
40312 | TimeSwHeat | Heating power in percent in timer interval | 0 | 100 | 0
40313 | TimeSwTemp | Temperature setpoint in timer interval | 5°C / 41°F | 45°C / 113°F | 21°C / 70°F
40314 | TimeSwFlow | Fan speed in percent in timer interval | 0 | 100 | 100
40315 | TimeSwMode | Automat or manual heating mode in timer interval | 0 | 2 | 0 | 0 = MANUAL 1 = AUTOMAT 2 = OFF MODE
40316 | TimeSw | Activation or deactivation actual timer interval | 0 | 1 | 0
40317 | default_cfg_restore | Forced configuration restore by button has be done | 0 | 1 | 0
40318 | Test_mode | Activation / deactivation of test mode | 0 | 1 | 0
40319 | Reserved | Reserved | 0 | 65535 | 0
40320 | Reserved | Reserved | 0 | 65535 | 0
40321 | Reserved | Reserved | 0 | 65535 | 0
40322 | Reserved | Reserved | 0 | 65535 | 0
40323 | Reserved | Reserved | 0 | 65535 | 0
40324 | Reserved | Reserved | 0 | 65535 | 0
40325 | Reserved | Reserved | 0 | 65535 | 0
40326 | Reserved | Reserved | 0 | 65535 | 0

## HOLDING-BMS_TEMP_SENSORS
Address | Name | Info
40100 | TempOutsideBMS | write temperature *10
40101 | OutsideTempSensorBmsSt | status of sensor
40102 | RoomBMS | write temperature *10
40103 | RoomTempSensorBmsSt | status of sensor